## Sheet1
HOLE | VALUE | DESCRIPTION | NAME | VALUE | COMMENT | ITEM | DESCRIPTION | PART NO. | QTY
F1 | 1.13 | 0.5 THRU | ISOX | 87.03 | ISO to ISO OVERALL WIDTH | 1 | 6" x 8.2# Structural Channel x 77.53 | 001 08405 006 | 1
F2 | 45.5 | 0.5 THRU | ISOZ | 43.61 | ISO to ISO OVERALL LENGTH | 2 | 6" x 8.2# Structural Channel x 77.53 | 001 08405 006 | 1
F3 | 30.9 | 0.5 THRU | D1 | 51.61 | TOTAL FAN SKID LENGTH | 3 | 6" x 8.2# Structural Channel x 47.77 | 001 08405 006 | 1
F4 | 11.92 | 0.5 THRU | D2 | 77.53 | TOTAL FAN SKID WIDTH | 4 | 6" x 8.2# Structural Channel x 47.77 | 001 08405 006 | 1
F5 | 31.76 | 0.5 THRU | D3 | 45.5 | INTERNAL DOA RAIL1 LOCATION | 5 | 6" x 8.2# Structural Channel x 47.77 | 001 08405 006 | 2
F6 | 7.93 | 0.5 THRU | D4 | 62.56 | INTERNAL DOA RAIL2 LOCATION | 6 | 4" x 5.4# Structural Channel x 21.25 | 001 08405 004 | 2
MB1 | 1.38 | 0.75 THRU | D5 | - | - | 7 | - | - | -
MB2 | 18.5 | 0.75 THRU | D6 | - | - | 8 | Isolator Support Angle - S1 Location | 091 20019 010 | 1
MB3 | 1.37 | 0.75 THRU | D7 | - | - | 9 | Isolator Support Angle - S2 Location | 091 20019 010 | 1
MB4 | 2 | 0.75 THRU | D8 | - | - | 10 | Isolator Support Angle - S3 Location | 091 20019 010 | 1
MB5 | 16 | 0.75 THRU | D9 | 1.92 | MOTOR SUP RAIL Z LOCATION | 11 | Isolator Support Angle - S4 Location | 091 20019 010 | 1
MB6 | - | - | D10 | 16 | MOTOR SUP RAIL SPACING
|  |  | D11 | 2.48 | MOTOR SUP RAIL, MOTOR SIDE OVERHANG
Parameter | Value | UM
Inside_Height | 106 | in
Inside_Width | 134 | in
Core_Segment_Length | 76 | in
MotorHand | 1 | ul
MotorLocation | 1 | ul
Tolerance_Gap | 0.031 | in
Side_BH_To_Shell_Clearance | 0.31 | in
Base_Fan_Z_Location | 48.69 | in
Base_Fan_Y_Location | 8.906 | in
Base_Fan_X_Location | 47.845 | in
FAN_Location_In_Segment | 2 | ul
FAN_FanType_Selection | 3 | ul
FAN_FanBlade_Direction | 1 | ul
FAN_WH_DIA_Nominal | 30 | in
FAN_LB | 1024 | in
FAN_Sheave_LB | 25 | in
FAN_A | 31.81 | in
FAN_B | 42.75 | in
FAN_BAH | 2.5 | in
FAN_BAW | 2.5 | in
FAN_BAT | 0.25 | in
FAN_BH | 0.56 | in
FAN_BH_NOM | 0.5 | in
FAN_DC | 24.5 | in
FAN_DD | 30.25 | in
FAN_DE | 14.75 | in
FAN_DX | 1.5 | in
FAN_G | 41 | in
FAN_GA | 0.126 | in
FAN_GB | 0.097 | in
FAN_GC | 20.5 | in
FAN_H | 47.75 | in
FAN_HE | 25.75 | in
FAN_HJ | 23.31 | in
FAN_HN | 31.75 | in
FAN_J | 26.25 | in
FAN_P | 32.88 | in
FAN_Q | 15.81 | in
FAN_SD | 2.4375 | in
FAN_KSL | 5.5 | in
FAN_KSW | 0.63 | in
FAN_KSD | 0.31 | in
FAN_AH | 1 | in
FAN_K | 22.75 | in
FAN_M | 15.88 | in
FAN_N | 1.13 | in
FAN_ND | 4.62 | in
FAN_WOD | 36 | in
FAN_WID | 23.4 | in
FAN_WW | 27.7875 | in
FAN_INLET_FLG_W | 1.5 | in
FAN_BRG_SUP_W | 3.5 | in
FAN_BRG_SUP_T | 0.375 | in
FAN_BRG_DIA | 3.6562 | in
FAN_BRG_W | 3 | in
FAN_BRG_H | 3.7812 | in
FAN_FRAME_CUT_FIA | 9.75 | in
FAN_FRAME_CUT_LIA | 0.063 | in
FAN_FRAME_TOP_Suppresion | 1 | ul
MTR_C | 30.28 | in
MTR_D | 8 | in
MTR_E | 6.25 | in
MTR_2F | 12 | in
MTR_H | 0.656 | in
MTR_P | 16.5 | in
MTR_KWL | 3.875 | in
MTR_R | 1.844 | in
MTR_S | 0.5 | in
MTR_U | 2.125 | in
MTR_V | 5.25 | in
MTR_AB | 14.61 | in
MTR_BA | 5.25 | in
MTR_BL | 14 | in
MTR_BW | 14.5 | in
MTR_D1 | 1 | in
MTR_D2 | 0.44 | in
MTR_LB | 700 | ul
MTR_Hand | 1 | ul
MTR_Beside_X_Location | 93.35 | in
MTR_Behind_X_Location | 62.6 | in
MTR_Y_Location | 12.99 | in
MTR_Beside_Z_Location | -15.88 | in
MTR_Behind_Z_Location | -15.88 | in
MTRBS_AL | 22.75 | in
MTRBS_AM | 20.75 | in
MTRBS_AX | 2.5 | in
MTRBS_BB | 15.5 | in
MTRBS_E | 6.25 | in
MTRBS_F | 6 | in
MTRBS_AO | 8 | in
MTRBS_AR | 9.25 | in
MTRBS_AU | 0.75 | in
MTRBS_BT | 5.25 | in
MTRBS_AT | 0.1875 | in
MTRBS_XC | 2.125 | in
MTRBS_DBOLT_D | 0.625 | in
MTRBS_DBOLT_L | 2.5 | in
MTRBS_AYBOLT_D | 0.75 | in
MTRBS_AYBOLT_L | 9 | in
MTRBS_LB | 31 | ul
MTRBS_AdjBolt_Loc | 6 | in
MTRBS_AdjBolt_ArrayQty | 2 | ul
MTRBS_AdjBolt_ArrayDist | 12 | in
MTRBS_Bstyle_Suppresion | 1 | ul
MTRBS_Bstyle_Flange_W | 4 | in
MTRBS_Bstyle_Block_W | 2 | in
MTRBS_X_Location | 93.35 | in
MTRBS_Y_Location | 10.49 | in
MTRBS_Z_Location | -15.88 | in
TopDischTrans_Y_Loc | 75.156 | in
TopDischTrans_Z_Loc | 41.285 | in
TopDischTrans_H | 12 | in
TopDischTrans_X | 42.388 | in
TopDischTrans_Z | 31.56 | in
TopDischTrans_FIA_LIA_L | 42.5 | in
TopDischTrans_RH_LH_L | 31.386 | in
TopDischTrans_Hole1_YLoc_Top | 0.75 | in
TopDischTrans_Hole1_YLoc_Btm | 1.375 | in
TopDischTrans_Hole1_ArrayQty | 3 | ul
TopDischTrans_Hole1_ArrayDist | 4.9375 | in
TopDischTrans_Stiffener_Flng_L | 1.25 | in
TopDischTrans_Stiffener_YLoc | 1.375 | in
TopDischTrans_Stiffener_ArrayQty | 1 | ul
TopDischTrans_Stiffener_ArrayDist | 6.25 | in
TopDischTrans_Stiffener_FIA_LIA_L | 42.5 | in
TopDischTrans_Stiffener_FIA_LIA_Hole1_XLoc | 1.5 | in
TopDischTrans_Stiffener_FIA_LIA_Hole1_ArrayQty | 6 | ul
TopDischTrans_Stiffener_FIA_LIA_Hole1_ArrayDist | 7.9 | in
TopDischTrans_Stiffener_RH_LH_L | 31.56 | in
TopDischTrans_Stiffener_RH_LH_Hole1_ZLoc | 2 | in
TopDischTrans_Stiffener_RH_LH_Hole1_ArrayQty | 5 | ul
TopDischTrans_Stiffener_RH_LH_Hole1_ArrayDist | 6.89 | in
TopDischTrans_Eng_Hole_Dia | 0.152 | in
TopDischTrans_Clr_Hole_Dia | 0.218 | in
TopDischTrans_Thk | 0.05601 | in
PLT_W | 9 | in
PLT_L | 13 | in
PLT_T | 0.15601 | in
PLT_PH | 0.25 | in
PLT_SH | 0.75 | in
PLTS1_Designation | 4 | ul
PLTS1_OS | 0 | ul
PLTS1_SS | 1 | ul
PLTS1_SW1 | 2.625 | in
PLTS1_SW2 | 6.375 | in
PLTS1_SL1 | 1.125 | in
PLTS1_SL2 | 6.5 | in
PLTS2_Designation | 3 | ul
PLTS2_OS | 1 | ul
PLTS2_SS | 0 | ul
PLTS2_SW1 | 1.125 | in
PLTS2_SW2 | 4.875 | in
PLTS2_SL1 | 3.8125 | in
PLTS2_SL2 | 9.1875 | in
PLTS3_Designation | 4 | ul
PLTS3_OS | 0 | ul
PLTS3_SS | 1 | ul
PLTS3_SW1 | 2.625 | in
PLTS3_SW2 | 6.375 | in
PLTS3_SL1 | 1.125 | in
PLTS3_SL2 | 6.5 | in
PLTS4_Designation | 3 | ul
PLTS4_OS | 1 | ul
PLTS4_SS | 0 | ul
PLTS4_SW1 | 1.125 | in
PLTS4_SW2 | 4.875 | in
PLTS4_SL1 | 3.8125 | in
PLTS4_SL2 | 9.1875 | in
ISO_S1_PartNumber | 11 | ul
ISO_S1_OPHGT | 7.25 | in
ISO_S1_BLT | 1.5 | in
ISO_S1_BW | 6 | in
ISO_S1_BL | 7.625 | in
ISO_S1_BT | 0.375 | in
ISO_S1_BHD | 0.875 | in
ISO_S1_BHW | 1.125 | in
ISO_S1_BHL | 1.125 | in
ISO_S1_HL | 6.44 | in
ISO_S1_TDBL | 2 | in
ISO_S1_TDBD | 0.5 | in
ISO_S1_ADJBD | 0.625 | in
ISO_S2_PartNumber | 14 | ul
ISO_S2_OPHGT | 7.25 | in
ISO_S2_BLT | 1.5 | in
ISO_S2_BW | 6 | in
ISO_S2_BL | 7.625 | in
ISO_S2_BT | 0.375 | in
ISO_S2_BHD | 0.875 | in
ISO_S2_BHW | 1.125 | in
ISO_S2_BHL | 1.125 | in
ISO_S2_HL | 6.44 | in
ISO_S2_TDBL | 2 | in
ISO_S2_TDBD | 0.5 | in
ISO_S2_ADJBD | 0.625 | in
ISO_S3_PartNumber | 12 | ul
ISO_S3_OPHGT | 7.25 | in
ISO_S3_BLT | 1.5 | in
ISO_S3_BW | 6 | in
ISO_S3_BL | 7.625 | in
ISO_S3_BT | 0.375 | in
ISO_S3_BHD | 0.875 | in
ISO_S3_BHW | 1.125 | in
ISO_S3_BHL | 1.125 | in
ISO_S3_HL | 6.44 | in
ISO_S3_TDBL | 2 | in
ISO_S3_TDBD | 0.5 | in
ISO_S3_ADJBD | 0.625 | in
ISO_S4_PartNumber | 12 | ul
ISO_S4_OPHGT | 7.25 | in
ISO_S4_BLT | 1.5 | in
ISO_S4_BW | 6 | in
ISO_S4_BL | 7.625 | in
ISO_S4_BT | 0.375 | in
ISO_S4_BHD | 0.875 | in
ISO_S4_BHW | 1.125 | in
ISO_S4_BHL | 1.125 | in
ISO_S4_HL | 6.44 | in
ISO_S4_TDBL | 2 | in
ISO_S4_TDBD | 0.5 | in
ISO_S4_ADJBD | 0.625 | in
ISO_TopNut_Plane_Loc | 0.5 | in
ISO_S1_XLoc | 106.2452 | in
ISO_S1_ZLoc | 68.5 | in
ISO_S2_XLoc | 106.2452 | in
ISO_S2_ZLoc | 24.89 | in
ISO_S3_XLoc | 19.2146 | in
ISO_S3_ZLoc | 68.5 | in
ISO_S4_XLoc | 19.2146 | in
ISO_S4_ZLoc | 24.89 | in
FanBase_Str_CHAN_Suppresion | 1 | ul
FanBase_Str_FIA_LIA_CHAN_XLoc | 14.8849 | in
FanBase_Str_FIA_CHAN_ZLoc | 21.85 | in
FanBase_Str_LIA_CHAN_ZLoc | 71.54 | in
FanBase_Str_FIA_LIA_CHAN_L | 77.5306 | in
FanBase_Str_FIA_LIA_CHAN_H | 6 | in
FanBase_Str_FIA_LIA_CHAN_D | 1.92 | in
FanBase_Str_FIA_LIA_CHAN_WT | 0.2 | in
FanBase_Str_FIA_LIA_CHAN_FTR | 0.343 | in
FanBase_Str_FIA_LIA_CHAN_LB | 52.9792 | ul
FanBase_Str_FIA_LIA_CHAN_Loc_Plane | 0.96 | in
FanBase_Str_DOA_CHAN_Suppresion | 1 | ul
FanBase_Str_DOA_CHAN_L | 47.77 | in
FanBase_Str_DOA_CHAN_H | 6 | in
FanBase_Str_DOA_CHAN_D | 1.92 | in
FanBase_Str_DOA_CHAN_WT | 0.2 | in
FanBase_Str_DOA_CHAN_FTR | 0.343 | in
FanBase_Str_DOA_CHAN_LB | 32.6428 | ul
FanBase_Str_DOA_CHAN_HoleLoc_Plane | 1.1304 | in
FanBase_Str_DOA_INT_MTR_CHAN_Coping_Suppresion | 0 | in
FanBase_Str_DOA_INT_MTR_CHAN_Suppresion | 1 | ul
FanBase_Str_DOA_INT_FAN_CHAN_Suppresion | 1 | ul
FanBase_Str_DOA_INT_MTR_CHAN_XLoc | 37.5446 | in
FanBase_Str_DOA_INT_MTR_CHAN_ZLoc | 46.695 | in
FanBase_Str_DOA_INT_FAN_CHAN_XLoc | 22.75 | in
FanBase_Str_DOA_INT_FAN_CHAN_ZLoc | 46.695 | in
FanBase_Str_DOA_INT_CHAN_L | 47.77 | in
FanBase_Str_DOA_INT_CHAN_H | 6 | in
FanBase_Str_DOA_INT_CHAN_LBFT | 8.2 | in
FanBase_Str_DOA_INT_CHAN_D | 1.92 | in
FanBase_Str_DOA_INT_CHAN_WT | 0.2 | in
FanBase_Str_DOA_INT_CHAN_FTR | 0.343 | in
FanBase_Str_DOA_INT_CHAN_LB | 32.6428 | ul
FanBase_Str_DOA_INT_FAN_CHAN_HoleLoc_Plane | 1.1304 | in
FanBase_Str_DOA_INT_MTR_CHAN_HoleLoc_Plane | 1.1304 | in
FanBase_Str_DOW_INT_CHAN_Suppresion | 0 | ul
FanBase_Str_DOW_INT_CHAN_XLoc | 47.9518 | in
FanBase_Str_DOW_INT_CHAN_ZLoc | 57.221 | in
FanBase_Str_DOW_INT_CHAN_L | 43.0256 | in
FanBase_Str_DOW_INT_CHAN_H | 6 | in
FanBase_Str_DOW_INT_CHAN_LBFT | 8.2 | in
FanBase_Str_DOW_INT_CHAN_D | 1.92 | in
FanBase_Str_DOW_INT_CHAN_WT | 0.2 | in
FanBase_Str_DOW_INT_CHAN_FTR | 0.343 | in
FanBase_Str_DOW_INT_CHAN_LB | 29.4008 | ul
FanBase_Str_MtrSup_CHAN_XLoc | 93.35 | in
FanBase_Str_MtrSup_CHAN_ZLoc | -15.88 | in
FanBase_Str_MtrSup_CHAN_Spacing | 16 | in
FanBase_Str_MtrSup_CHAN_L | 21.25 | in
FanBase_Str_MtrSup_CHAN_H | 4 | in
FanBase_Str_MtrSup_CHAN_D | 1.584 | in
FanBase_Str_MtrSup_CHAN_WT | 0.184 | in
FanBase_Str_MtrSup_CHAN_FTR | 0.296 | in
FanBase_Str_MtrSup_CHAN_LB | 9.5625 | ul
FanBase_Str_IsoSup_ANG_Suppresion | 1 | ul
FanBase_Str_IsoSup_ANG_Designation_S1_Loc | 2 | ul
FanBase_Str_IsoSup_ANG_S1_Gusset_Suppresion | 0 | ul
FanBase_Str_IsoSup_ANG_Designation_S2_Loc | 2 | ul
FanBase_Str_IsoSup_ANG_S2_Gusset_Suppresion | 0 | ul
FanBase_Str_IsoSup_ANG_Designation_S3_Loc | 2 | ul
FanBase_Str_IsoSup_ANG_S3_Gusset_Suppresion | 0 | ul
FanBase_Str_IsoSup_ANG_Designation_S4_Loc | 2 | ul
FanBase_Str_IsoSup_ANG_S4_Gusset_Suppresion | 0 | ul
FanBase_Str_IsoSup_ANG_H | 4 | in
FanBase_Str_IsoSup_ANG_D | 6 | in
FanBase_Str_IsoSup_ANG_L | 8 | in
FanBase_Str_IsoSup_ANG_WT | 0.5 | in
FanBase_Str_IsoSup_ANG_FTR | 0.5 | in
FanBase_Str_IsoSup_ANG_HS | 2 | in
FanBase_Str_IsoSup_ANG_HL | 1.25 | in
FanBase_Str_IsoSup_ANG_HD1 | 0.625 | in
FanBase_Str_IsoSup_ANG_HD2 | 0.875 | in
FanBase_Str_IsoSup_ANG_LB | 10.8 | ul
FanBase_Str_IsoSup_ANG_Offset_S1_Loc | 1 | in
FanBase_Str_IsoSup_ANG_Offset_S2_Loc | 1 | in
FanBase_Str_IsoSup_ANG_Offset_S3_Loc | 1 | in
FanBase_Str_IsoSup_ANG_Offset_S4_Loc | 1 | in
FanBase_Str_IsoSup_ANG_Overhang | 1.92 | in
FanBase_Str_ANG_Suppresion | 0 | ul
FanBase_Str_DOA_ANG_IsoHole_STLOC | 0.75 | in
FanBase_Str_DOA_ANG_IsoHole_HS | 2 | in
FanBase_Str_DOA_ANG_IsoHole_HL | 1.25 | in
FanBase_Str_DOA_ANG_IsoHole_HD1 | 0.625 | in
FanBase_Str_DOA_ANG_IsoHole_HD2 | 0.875 | in
FanBase_Str_FIA_ANG_L | 74.63 | in
FanBase_Str_FIA_ANG_H | 4 | in
FanBase_Str_FIA_ANG_D | 3 | in
FanBase_Str_FIA_ANG_WT | 0.375 | in
FanBase_Str_FIA_ANG_FTR | 0.5 | in
FanBase_Str_FIA_ANG_LB | 52.8629 | ul
FanBase_Str_FIA_ANG_XLoc | 15.94 | in
FanBase_Str_FIA_ANG_ZLoc | 24.81 | in
FanBase_Str_MIA_ANG_Suppresion | 0 | ul
FanBase_Str_MIA_ANG_L | 74.63 | in
FanBase_Str_MIA_ANG_H | 4 | in
FanBase_Str_MIA_ANG_D | 3 | in
FanBase_Str_MIA_ANG_WT | 0.375 | in
FanBase_Str_MIA_ANG_FTR | 0.5 | in
FanBase_Str_MIA_ANG_LB | 52.8629 | ul
FanBase_Str_MIA_ANG_HoleLoc_Plane | 1.5 | in
FanBase_Str_MIA_ANG_ZLoc | 40.81 | in
FanBase_Str_LIA_ANG_L | 74.63 | in
FanBase_Str_LIA_ANG_H | 4 | in
FanBase_Str_LIA_ANG_D | 3 | in
FanBase_Str_LIA_ANG_WT | 0.375 | in
FanBase_Str_LIA_ANG_FTR | 0.5 | in
FanBase_Str_LIA_ANG_LB | 52.8629 | ul
FanBase_Str_LIA_ANG_HoleLoc_Plane | 1.5 | in
FanBase_Str_LIA_ANG_ZLoc | 71 | in
FanBase_Str_DB_ANG_Suppresion | 0 | ul
FanBase_Str_DB_ANG_L | 42.75 | in
FanBase_Str_DB_ANG_H | 4 | in
FanBase_Str_DB_ANG_D | 3 | in
FanBase_Str_DB_ANG_WT | 0.375 | in
FanBase_Str_DB_ANG_FTR | 0.5 | in
FanBase_Str_DB_ANG_LB | 30.2812 | ul
FanBase_Str_DB_ANG_HoleLoc_Plane | 1.5 | in
FanBase_Str_DB_ANG_ZLoc | 58.69 | in
FanBase_Str_DOA_ANG_L | 53.315 | in
FanBase_Str_DOA_ANG_H | 6 | in
FanBase_Str_DOA_ANG_D | 4 | in
FanBase_Str_DOA_ANG_WT | 0.375 | in
FanBase_Str_DOA_ANG_FTR | 0.5 | in
FanBase_Str_DOA_ANG_LB | 54.6479 | ul
FanBase_Str_DOA_ANG_ZLoc | 45.8425 | in
FanBase_Str_DOA_INT_ANG_Suppresion | 0 | ul
FanBase_Str_DOA_INT_ANG_RH_Location | 70.72 | in
FanBase_Str_DOA_INT_ANG_LH_Location | 84.1 | in
FanBase_Str_DOA_INT_ANG_L | 43.19 | in
FanBase_Str_DOA_INT_ANG_H | 4 | in
FanBase_Str_DOA_INT_ANG_D | 3 | in
FanBase_Str_DOA_INT_ANG_WT | 0.375 | in
FanBase_Str_DOA_INT_ANG_FTR | 0.5 | in
FanBase_Str_DOA_INT_ANG_LB | 30.5929 | ul
FanBase_Str_DOA_INT_ANG_HoleLoc_Plane | 1.5 | in
FanBase_Str_Inertia_Plate1_Suppresion | 0 | ul
FanBase_Str_Inertia_Plate2_Suppresion | 0 | ul
FanBase_Str_Inertia_Plate3_Suppresion | 0 | ul
FanBase_Str_Inertia_Plate4_Suppresion | 0 | ul
FanBase_Str_Inertia_Plate5_Suppresion | 0 | ul
FanBase_Str_Inertia_PlateBeside_Btm_Suppresion | 0 | ul
FanBase_Str_Inertia_PlateBeside_BtmFiller_Suppresion | 0 | ul
FanBase_Str_Inertia_PlateBeside_BtmInvFiller_Suppresion | 0 | ul
FanBase_Str_Inertia_Plate_Qty | 0 | ul
FanBase_Str_Inertia_Plate_Thk | 0.05601 | in
FanBase_Str_Inertia_Plate_YLoc | 2.906 | in
FanBase_Str_Inertia_Plate_XLoc | 14.8849 | in
FanBase_Str_Inertia_Plate_FlangeH | 1.75 | in
FanBase_Str_Inertia_Plate_Flange_EndNotch | 1.545 | in
FanBase_Str_Inertia_Plate_Flange_BtmInvDischNotch_Suppresion | 0 | ul
FanBase_Str_Inertia_Plate_Flange_BtmDischNotch_Suppresion | 0 | ul
FanBase_Str_Inertia_Plate_Flange_SnglPlateNotch_Suppresion | 0 | ul
FanBase_Str_Inertia_Plate_Flange_BtmDischNotch_XDim | 9.84 | in
FanBase_Str_Inertia_Plate_Flange_BtmDischNotch_XLoc | 33.3453 | in
FanBase_Str_Inertia_Plate_Flange_IntFanNotch_XLoc | 6.66 | in
FanBase_Str_Inertia_Plate_Flange_IntFanNotch_Suppresion | 1 | ul
FanBase_Str_Inertia_Plate_Flange_IntMtrNotch_XLoc | 11.14 | in
FanBase_Str_Inertia_Plate_Flange_IntMtrNotch_BtmFiller_XLoc | -52.0706 | in
FanBase_Str_Inertia_Plate_Flange_IntNotch_W | 2.42 | in
FanBase_Str_Inertia_Plate_X_Hole_YLoc | 0.875 | in
FanBase_Str_Inertia_Plate_X_Hole_BtmFiller_StartPlane | 63.2106 | in
FanBase_Str_Inertia_Plate_X_Hole_Eng_Hole_Dia | 0.152 | in
FanBase_Str_Inertia_Plate_X_Hole_Clr_Hole_Dia | 0.218 | in
FanBase_Str_Inertia_Plate_X_Hole_Ind_Hole_Dia | 0.125 | in
FanBase_Str_Inertia_Plate_X_Hole1_PlateBeside_Btm_Suppresion | 0 | ul
FanBase_Str_Inertia_Plate_X_Hole1_Suppresion | 0 | ul
FanBase_Str_Inertia_Plate_X_Hole1_XLoc | 2.375 | in
FanBase_Str_Inertia_Plate_X_Hole1_ArrayQty | 2 | ul
FanBase_Str_Inertia_Plate_X_Hole1_ArrayDist | 1.91 | in
FanBase_Str_Inertia_Plate_X_Hole2_Suppresion | 1 | ul
FanBase_Str_Inertia_Plate_X_Hole2_XLoc | 9.035 | in
FanBase_Str_Inertia_Plate_X_Hole2_ArrayQty | 0 | ul
FanBase_Str_Inertia_Plate_X_Hole2_ArrayDist | 0.27 | in
FanBase_Str_Inertia_Plate_X_Hole3_Suppresion | 1 | ul
FanBase_Str_Inertia_Plate_X_Hole3_XLoc | 13.515 | in
FanBase_Str_Inertia_Plate_X_Hole3_ArrayQty | 2 | ul
FanBase_Str_Inertia_Plate_X_Hole3_ArrayDist | 1.91 | in
FanBase_Str_Inertia_Plate1_ZDim | 12 | in
FanBase_Str_Inertia_Plate1_XDim | 76.5306 | in
FanBase_Str_Inertia_Plate1_ZLoc | 27.39 | in
FanBase_Str_Inertia_Plate2_ZDim | 12 | in
FanBase_Str_Inertia_Plate2_XDim | 76.5306 | in
FanBase_Str_Inertia_Plate2_ZLoc | 39.39 | in
FanBase_Str_Inertia_Plate3_ZDim | 12 | in
FanBase_Str_Inertia_Plate3_XDim | 76.5306 | in
FanBase_Str_Inertia_Plate3_ZLoc | 51.39 | in
FanBase_Str_Inertia_Plate4_ZDim | 12 | in
FanBase_Str_Inertia_Plate4_XDim | 76.5306 | in
FanBase_Str_Inertia_Plate4_ZLoc | 63.39 | in
FanBase_Str_Inertia_Plate5_ZDim | 12 | in
FanBase_Str_Inertia_Plate5_XDim | 76.5306 | in
FanBase_Str_Inertia_Plate5_ZLoc | 39.39 | in
FanBase_Str_Inertia_PlateBeside_Btm_ZDim | 12 | in
FanBase_Str_Inertia_PlateBeside_Btm_XDim | 76.5306 | in
FanBase_Str_Inertia_PlateBeside_Btm_ZLoc | 39.39 | in
FanBase_Str_Inertia_PlateBeside_BtmFiller_ZDim | 12 | in
FanBase_Str_Inertia_PlateBeside_BtmFiller_XDim | 13.32 | in
FanBase_Str_Inertia_PlateBeside_BtmFiller_ZLoc | 39.39 | in
FanBase_Str_Inertia_PlateBeside_BtmFiller_XLoc | 46.4902 | in
FanBase_Str_Inertia_PlateBeside_BtmInvFiller_ZDim | 12 | in
FanBase_Str_Inertia_PlateBeside_BtmInvFiller_XDim | 13.32 | in
FanBase_Str_Inertia_PlateBeside_BtmInvFiller_ZLoc | 27.39 | in
FanBase_Str_Inertia_PlateBeside_BtmInvFiller_XLoc | 46.4902 | in
FanBase_Str_Inertia_Rebar_D | 0.5 | in
FanBase_Str_Inertia_Rebar_Zone1_Suppresion | 0 | ul
FanBase_Str_Inertia_Rebar_Zone2_Suppresion | 0 | ul
FanBase_Str_Inertia_Rebar_Zone3_Suppresion | 0 | ul
FanBase_Str_Inertia_Rebar_YLoc | 4.906 | in
FanBase_Str_Inertia_Rebar_Zone1_XLength | 5.75 | in
FanBase_Str_Inertia_Rebar_Zone1_ZLength | 11.75 | in
FanBase_Str_Inertia_Rebar_Zone1_XArray_XStart | 4.92 | in
FanBase_Str_Inertia_Rebar_Zone1_XArray_ZStart | 46.695 | in
FanBase_Str_Inertia_Rebar_Zone1_XArrayQty | 1 | ul
FanBase_Str_Inertia_Rebar_Zone1_XArrayDist | 6 | in
FanBase_Str_Inertia_Rebar_Zone1_ZArray_XStart | 3.2 | in
FanBase_Str_Inertia_Rebar_Zone1_ZArray_ZStart | 43.695 | in
FanBase_Str_Inertia_Rebar_Zone1_ZArrayQty | 2 | ul
FanBase_Str_Inertia_Rebar_Zone1_ZArrayDist | 6 | in
FanBase_Str_Inertia_Rebar_Zone2_XLength | 5.75 | in
FanBase_Str_Inertia_Rebar_Zone2_ZLength | 47.52 | in
FanBase_Str_Inertia_Rebar_Zone2_XArray_XStart | 9.4 | in
FanBase_Str_Inertia_Rebar_Zone2_XArray_ZStart | 46.695 | in
FanBase_Str_Inertia_Rebar_Zone2_XArrayQty | 1 | ul
FanBase_Str_Inertia_Rebar_Zone2_XArrayDist | 6 | in
FanBase_Str_Inertia_Rebar_Zone2_ZArray_XStart | 9.4 | in
FanBase_Str_Inertia_Rebar_Zone2_ZArray_ZStart | 28.695 | in
FanBase_Str_Inertia_Rebar_Zone2_ZArrayQty | 5 | ul
FanBase_Str_Inertia_Rebar_Zone2_ZArrayDist | 9 | in
FanBase_Str_Inertia_Rebar_Zone3_XLength | 5.75 | in
FanBase_Str_Inertia_Rebar_Zone3_ZLength | 47.52 | in
FanBase_Str_Inertia_Rebar_Zone3_XArray_XStart | 15.6 | in
FanBase_Str_Inertia_Rebar_Zone3_XArray_ZStart | 46.695 | in
FanBase_Str_Inertia_Rebar_Zone3_XArrayQty | 1 | ul
FanBase_Str_Inertia_Rebar_Zone3_XArrayDist | 6 | in
FanBase_Str_Inertia_Rebar_Zone3_ZArray_XStart | 15.6 | in
FanBase_Str_Inertia_Rebar_Zone3_ZArray_ZStart | 28.695 | in
FanBase_Str_Inertia_Rebar_Zone3_ZArrayQty | 5 | ul
FanBase_Str_Inertia_Rebar_Zone3_ZArrayDist | 9 | in
WLDMNT_FIA_LIA_Direction | 2 | ul
WLDMNT_Base_THK | 0.25 | in
WLDMNT_Base_L | 38.5 | in
WLDMNT_Base_W | 50 | in
WLDMNT_Base_H | 6 | in
WLDMNT_Base4_FIA_FlngD | 3 | in
WLDMNT_Base4_LIA_FlngD | 3 | in
WLDMNT_Base4_FIA_Loc | 19.25 | in
WLDMNT_Base4_LIA_Loc | 19.25 | in
WLDMNT_Base6_DOA_Suppresion | 1 | ul
WLDMNT_IntRail_DOA_ZLoc | 19.25 | in
WLDMNT_IntRail_DOA_XLoc | 5.5556 | in
WLDMNT_IntRail_DOA_L | 38.498 | in
WLDMNT_IntRail_DOA_Base4_BS_Suppresion | 0 | ul
WLDMNT_IntRail_DOA_Base4_BH_Suppresion | 0 | ul
WLDMNT_IntRail_DOA_Base4_LH_Suppresion | 0 | ul
WLDMNT_IntRail_DOA_Base4_RH_Suppresion | 0 | ul
WLDMNT_IntRail_DOA_Base6_LH_Suppresion | 1 | ul
WLDMNT_IntRail_DOA_Base6_RH_Suppresion | 0 | ul
WLDMNT_IntRail_DOA_Rail1_Loc | 4 | in
WLDMNT_IntRail_DOA_Rail2_Loc | 12 | in
WLDMNT_IntRail_DOA_Rail1_Suppresion | 1 | ul
WLDMNT_IntRail_DOA_Rail2_Suppresion | 1 | ul
WLDMNT_IntRail_DOA_Rail1_BBH_LIA_Suppresion | 0 | ul
WLDMNT_IntRail_DOA_Rail2_BBH_LIA_Suppresion | 0 | ul
WLDMNT_IntRail_DOA_Rail1_BBH_FIA_Suppresion | 0 | ul
WLDMNT_IntRail_DOA_Rail2_BBH_FIA_Suppresion | 0 | ul
WLDMNT_IntRail_DOA_Coping_Suppresion | 0 | ul
WLDMNT_IntRail_DOW_ZLoc | -10 | in
WLDMNT_IntRail_DOW_Zloc_BtmDisch | -1 | in
WLDMNT_IntRail_DOW_XLoc | -9.5 | in
WLDMNT_IntRail_DOW_L | 28.748 | in
WLDMNT_IntRail_DOW_BtmDisch_Base4_Suppresion | 0 | ul
WLDMNT_IntRail_DOW_Base4_Suppresion | 0 | ul
WLDMNT_IntRail_DOW_Base6_Suppresion | 0 | ul
WLDMNT_IsoSupAng_ZLoc | 21.251 | in
WLDMNT_IsoSupAng_XLoc | 25.001 | in
WLDMNT_MtrRail_L | 17 | in
WLDMNT_MtrRail_Spacing | 12 | in
WLDMNT_MtrRail_XLoc | 17 | in
WLDMNT_MtrRail_ZLoc | -11.25 | in
WLDMNT_FanHole_Dia | 0.5 | in
WLDMNT_FanHole_Spacing_Z | 15.4 | in
WLDMNT_FanHole_Spacing_X | 28.748 | in
WLDMNT_FanHole_XLoc | -9.5 | in
WLDMNT_FanHole_ZLoc | 6.55 | in
WLDMNT_FanHole_6_RHSuppresion_BH | 0 | ul
WLDMNT_FanHole_6_RHSuppresion_BS | 0 | ul
WLDMNT_FanHole_6_LHSuppresion_BH | 0 | ul
WLDMNT_FanHole_6_LHSuppresion_BS | 1 | ul
WLDMNT_FanHole_6_RHSuppresion_BBH | 0 | ul
WLDMNT_FanHole_6_RHSuppresion_BBS | 0 | ul
WLDMNT_FanHole_6_LHSuppresion_BBH | 0 | ul
WLDMNT_FanHole_6_LHSuppresion_BBS | 0 | ul
WLDMNT_MtrBaseHole_Dia | 0.75 | in
WLDMNT_MtrBaseHole_Spacing_Z | 12 | in
WLDMNT_MtrBaseHole_Spacing_X | 15 | in
WLDMNT_MtrBaseHole_XLoc | 17 | in
WLDMNT_MtrBaseHole_ZLoc | -11.25 | in
WLDMNT_MtrBaseHole_4_RHSuppresion_BH | 0 | ul
WLDMNT_MtrBaseHole_4_RHSuppresion_BS | 0 | ul
WLDMNT_MtrBaseHole_4_LHSuppresion_BH | 0 | ul
WLDMNT_MtrBaseHole_4_LHSuppresion_BS | 0 | ul
WLDMNT_MtrBaseHole_6_RHSuppresion_BH | 0 | ul
WLDMNT_MtrBaseHole_6_RHSuppresion_BS | 0 | ul
WLDMNT_MtrBaseHole_6_LHSuppresion_BH | 0 | ul
WLDMNT_MtrBaseHole_6_LHSuppresion_BS | 1 | ul
WLDMNT_IsoHole_ZLoc | 17.251 | in
WLDMNT_IsoHole_XLoc | 29.75 | in
WLDMNT_ISOX | 87.03 | in
WLDMNT_ISOZ | 43.61 | in
S1_PLATE_ASY | 4 | ul
S2_PLATE_ASY | 3 | ul
S3_PLATE_ASY | 4 | ul
S4_PLATE_ASY | 3 | ul

## Data
INPUTS
Parameter | Value | Description |  | THIS BOX IS OUTPUT ONLY … DO NOT USE AS INPUTS
IH | 106 | Inside Height |  | Thickness Outputs
IW | 134 | Inside Width |  | InertiaPlateThk | 0.05601 | INERTIA FAN BASE SHEETMETAL BTM PANEL THICKNESS
SEGL | 76 | Segment Length |  | TopDischTransThk | 0.05601 | TOP DISCHARGE TRANSITION THICKNESS
FANSIZE | 300 | 122 to 600 Class 1 & 2 182 to 600 Class 3
FANCLASS | 2 | Fan Class 1, 2 or 3 | 1, 2, 3
FANWEIGHT | 1024 | Standard Fan Weights extracted from XML by MOM - Can be used as manual override for SQ purposes.
FANDISCHARGELOC | R | F, FI, R, RI, T, TI, B, BI (Front, Front Inverted, Rear, Rear Inverted, Top, Top Inverted, Btm, Btm Inverted) | F, FI, R, RI, T, TI, B, BI
MOTORFRAME | 326T | Motor Frame Size
MOTORLOCATION | BESIDE | BESIDE or BEHIND | BESIDE, BEHIND
MOTORHAND | L | L or R (Left or Right looking at air entering side of fan with airflow at your back) | L, R
MOTORWEIGHT | 700 | Standard Motor Weights extracted from XML by MOM - Can be used as manual override for SQ purposes. Edit manual (section 003) contains documentation on motor weights
FAN_X_LOCATION | 47.845 | Location of "Base" fan in X direction (across width of unit). Dim is from RH origin plane (RH side of IW of unit) to center of Fan Discharge Default = 0 - Default value centers fan discharge in IW of unit
ISOLATORDEFLECTION | 2 | 1 or 2 - Default = 2 | 1, 2
INERTIA | NO | YES or NO - Default = NO - Smaller fans that default to Type A base are forced to Type B when inertia is selected | Yes, No
MaterialStyle | STL GALV | Material Style | STL GALV, SST304
Construction | BASELINE | See "Isolator Plate" tab | BASELINE, SEISMIC
Fan_Start | 0 | Distance from segment start to fan discharge start - Default = 0"
Motor_ChannelO | 0 | Only valid Channel sizes from steel list can be used. Enter as Channel Height followed a space followed by LB/FT (ie. 3 4.1 is 3" channel 4.1 lb/ft) - Default = 0
FanBase_Type_ForcedO | - | "-", TYPEA, TYPEB, or TYPEC - Forces fan base to Type A, B or C regardless of fan size - STD = TypeA fan <=222, TypeB fan >222 and <=365, TypeC fan >365 - Default = "-" | -, TYPEA, TYPEB, or TYPEC
Center_DistanceO | 0 | Center Distance override - Default = 0
InertiaPlateThkO | - | Inertia Bottom Plate Thickness Override - set to "-" when using defaults - Default = 16ga
TopDischTransThkO | - | Top Discharge Transition Thickness Override - set to "-" when using defaults - Default = 16ga

## Excel Calcs
2.34
Parameter | Value |  | Parameter | Value | Parameter | Value | Parameter | Value | Parameter | Value | Parameter | Value
General |  |  | Motor Data |  | Isolator Plate Data |  | Structural Fan Base Data Type B & C |  | Structural Fan Base Data Type A |  | Inertia Base Data
Sheetmetal Weight lb/sqft/in | 40.793 |  | MTR_C | 30.28 | PLT_W | 9 | Min_Dist_HoleCtr_To_SteelWeb_FIA/LIA/DOA_Rail | 1.1304 | Min_Dist_HoleCtr_To_SteelWeb_DOA_Rail | 1.5 | FanBase_Str_Inertia_Internal_DOA_ChannelSpace | 4.42
Inside Height | 106 |  | MTR_D | 8 | PLT_L | 13 | DOA_INT_MTR_CHAN_to_MTRBS_Hole | 0.5 | Min_Dist_HoleCtr_To_SteelWeb_FIA/LIA_Rail | 1.364 | FanBase_Str_Inertia_BtmPlate_OutsideTollerance | 0.5
Inside Width | 134 |  | MTR_E | 6.25 | PLT_T | 0.15601 | FIAtoLIA_Channel_Distance | 51.61 | Min_Dist_FanMntHole_to_FIA/LIA_Rail | 1.364 | FanBase_Str_Inertia_Total_Plate_XDim | 76.5306
Core_Segment_Length | 76 |  | MTR_2F | 12 | PLT_PH | 0.25 | FanFace_to_StructBaseFace | 0.5 | FIAtoLIA_Angle_Distance | 49.19 | FanBase_Str_Inertia_Total_Plate_ZDim | 50.61
MotorHand | 1 |  | MTR_H | 0.656 | PLT_SH | 0.75 | FanBase_Str_CHAN_Suppresion | 1 | FanFace_to_StructBaseFace | 0.5 | FanBase_Str_Inertia_MaxPlate_XDim | 36
MotorLocation | 1 |  | MTR_P | 16.5 | PLT_Upstream_SLI | 6.5 | FIA/LIA Channel Data |  | FanBase_Str_ANG_Suppresion | 0 | FanBase_Str_Inertia_Plate1_Suppresion | 0
Tolerance_Gap | 0.031 |  | MTR_KWL | 3.875 | PLT_Dnstream_SLI | 9.1875 | FanBase_Str_FIA_LIA_CHAN_XLoc | 14.8849 | Isolator Hole Data |  | FanBase_Str_Inertia_Plate2_Suppresion | 0
Fan_BtmDisch_Tolerance_Gap | 0.031 |  | MTR_R | 1.844 | PLTS1_Designation | 4 | FanBase_Str_FIA_CHAN_ZLoc | 21.85 | FanBase_Str_DOA_ANG_IsoHole_STLOC | 0.75 | FanBase_Str_Inertia_Plate3_Suppresion | 0
Side BH to Shell Clearance | 0.31 |  | MTR_S | 0.5 | PLTS1_OS | 0 | FanBase_Str_LIA_CHAN_ZLoc | 71.54 | FanBase_Str_DOA_ANG_IsoHole_HS | 2 | FanBase_Str_Inertia_Plate4_Suppresion | 0
Fan_Disch_X_Distance (F, FI, R, RI) | 4 |  | MTR_U | 2.125 | PLTS1_SS | 1 | FanBase_Str_FIA_LIA_CHAN_Lookup | Channel68.2 | FanBase_Str_DOA_ANG_IsoHole_HL | 1.25 | FanBase_Str_Inertia_Plate5_Suppresion | 0
Fan_Disch_X_Distance (T, TI, B, BI) | 7 |  | MTR_V | 5.25 | PLTS1_SW1 | 2.625 | FanBase_Str_FIA_LIA_CHAN_L | 77.5306 | FanBase_Str_DOA_ANG_IsoHole_HD1 | 0.625 | FanBase_Str_Inertia_PlateBeside_Btm_Suppresion | 0
Base_Fan_Z_Location | 48.69 |  | MTR_AB | 14.61 | PLTS1_SW2 | 6.375 | FanBase_Str_FIA_LIA_CHAN_H | 6 | FanBase_Str_DOA_ANG_IsoHole_HD2 | 0.875 | FanBase_Str_Inertia_PlateBeside_BtmFiller_Suppresion | 0
Base_Fan_Y_Location | 8.906 |  | MTR_BA | 5.25 | PLTS1_SL1 | 1.125 | FanBase_Str_FIA_LIA_CHAN_LBFT | 8.2 | FIA Angle Data |  | FanBase_Str_Inertia_PlateBeside_BtmInvFiller_Suppresion | 0
Base_Fan_X_Location | 47.845 |  | MTR_BL | 14 | PLTS1_SL2 | 6.5 | FanBase_Str_FIA_LIA_CHAN_D | 1.92 | FanBase_Str_FIA_ANG_Lookup | Angle430.375 | FanBase_Str_Inertia_Plate_Qty | 0
MtrBehind_MinDistance_FanToMtr | 0.5 |  | MTR_BW | 14.5 | PLTS2_Designation | 3 | FanBase_Str_FIA_LIA_CHAN_WT | 0.2 | FanBase_Str_FIA_ANG_L | 74.63 | FanBase_Str_Inertia_Plate_Thk | 0.05601
Min_Isolator_CntrDist_DOA | 15.9375 |  | MTR_D1 | 1 | PLTS2_OS | 1 | FanBase_Str_FIA_LIA_CHAN_FTR | 0.343 | FanBase_Str_FIA_ANG_H | 4 | FanBase_Str_Inertia_Plate_GA | 16
FanBase_Type | TYPEB |  | MTR_D2 | 0.44 | PLTS2_SS | 0 | FanBase_Str_FIA_LIA_CHAN_LB | 52.9792 | FanBase_Str_FIA_ANG_D | 3 | FanBase_Str_Inertia_Plate_YLoc | 2.906
Isolator_Deflection | 2 |  | MTR_LB | 700 | PLTS2_SW1 | 1.125 | FanBase_Str_FIA_LIA_CHAN_Loc_Plane | 0.96 | FanBase_Str_FIA_ANG_WT | 0.375 | FanBase_Str_Inertia_Plate_XLoc | 14.8849
|  |  | MTR_Sheave_LB | 25 | PLTS2_SW2 | 4.875 | DOA Channel Data |  | FanBase_Str_FIA_ANG_FTR | 0.5 | FanBase_Str_Inertia_Plate_FlangeH | 1.75
Parameter | Value |  | MTR_Hand | 1 | PLTS2_SL1 | 3.8125 | FanBase_Str_DOA_CHAN_Suppresion | 1 | FanBase_Str_FIA_ANG_LB | 52.8629 | FanBase_Str_Inertia_Plate_Flange_EndNotch | 1.545
Fan Data |  |  | MTR_Beside_X_Location | 93.35 | PLTS2_SL2 | 9.1875 | FanBase_Str_DOA_CHAN_Lookup | Channel68.2 | FanBase_Str_FIA_ANG_HoleLoc_Plane | 1.5 | FanBase_Str_Inertia_Plate_Flange_BtmInvDischNotch_Suppresion | 0
FAN_Lookup | 300H |  | MTR_Behind_X_Location | 62.6 | PLTS3_Designation | 4 | FanBase_Str_DOA_CHAN_L | 47.77 | FanBase_Str_FIA_ANG_XLoc | 15.94 | FanBase_Str_Inertia_Plate_Flange_BtmDischNotch_Suppresion | 0
FAN_Location_In_Segment | LIA |  | MTR_Y_Location | 12.99 | PLTS3_OS | 0 | FanBase_Str_DOA_CHAN_H | 6 | FanBase_Str_FIA_ANG_ZLoc | 24.81 | FanBase_Str_Inertia_Plate_Flange_SnglPlateNotch_Suppresion | 0
FAN_FanType_Selection | 3 |  | MTR_Beside_Z_Location | -15.88 | PLTS3_SS | 1 | FanBase_Str_DOA_CHAN_LBFT | 8.2 | MIA Angle Data |  | FanBase_Str_Inertia_Plate_Flange_BtmDischNotch_XDim | 9.84
FAN_FanBlade_Direction | 1 |  | MTR_Behind_Z_Location | -15.88 | PLTS3_SW1 | 2.625 | FanBase_Str_DOA_CHAN_D | 1.92 | FanBase_Str_MIA_ANG_Suppresion | 0 | FanBase_Str_Inertia_Plate_Flange_BtmDischNotch_XLoc | 33.3453
FAN_WH_DIA_Nominal | 30 |  |  |  | PLTS3_SW2 | 6.375 | FanBase_Str_DOA_CHAN_WT | 0.2 | FanBase_Str_MIA_ANG_Lookup | Angle430.375 | FanBase_Str_Inertia_Plate_Flange_IntFanNotch_XLoc | 6.66
FAN_LB | 1024 |  | Parameter | Value | PLTS3_SL1 | 1.125 | FanBase_Str_DOA_CHAN_FTR | 0.343 | FanBase_Str_MIA_ANG_L | 74.63 | FanBase_Str_Inertia_Plate_Flange_IntFanNotch_Suppresion | 1
FAN_Sheave_LB | 25 |  | Motor Base Data |  | PLTS3_SL2 | 6.5 | FanBase_Str_DOA_CHAN_LB | 32.6428 | FanBase_Str_MIA_ANG_H | 4 | FanBase_Str_Inertia_Plate_Flange_IntMtrNotch_XLoc | 11.14
FAN_A | 31.81 |  | MTRBS_AL | 22.75 | PLTS4_Designation | 3 | FanBase_Str_DOA_CHAN_HoleLoc_Plane | 1.1304 | FanBase_Str_MIA_ANG_D | 3 | FanBase_Str_Inertia_Plate_Flange_IntMtrNotch_BtmFiller_XLoc | -52.0706
FAN_B | 42.75 |  | MTRBS_AM | 20.75 | PLTS4_OS | 1 | DOA Internal Channel Data |  | FanBase_Str_MIA_ANG_WT | 0.375 | FanBase_Str_Inertia_Plate_Flange_IntNotch_W | 2.42
FAN_BAH | 2.5 |  | MTRBS_AX | 2.5 | PLTS4_SS | 0 | FanBase_Str_DOA_INT_MTR_CHAN_Coping_Suppresion | 0 | FanBase_Str_MIA_ANG_FTR | 0.5 | FanBase_Str_Inertia_Plate_X_Hole_XStart | 2.375
FAN_BAW | 2.5 |  | MTRBS_BB | 15.5 | PLTS4_SW1 | 1.125 | FanBase_Str_DOA_INT_MTR_CHAN_Suppresion | 1 | FanBase_Str_MIA_ANG_LB | 52.8629 | FanBase_Str_Inertia_Plate_X_Hole_YLoc | 0.875
FAN_BAT | 0.25 |  | MTRBS_BT | 5.25 | PLTS4_SW2 | 4.875 | FanBase_Str_DOA_INT_FAN_CHAN_Suppresion | 1 | FanBase_Str_MIA_ANG_HoleLoc_Plane | 1.5 | FanBase_Str_Inertia_Plate_X_Hole_BtmFiller_StartPlane | 63.2106
FAN_BH | 0.56 |  | MTRBS_E | 6.25 | PLTS4_SL1 | 3.8125 | FanBase_Str_DOA_INT_MTR_CHAN_XLoc | 37.5446 | FanBase_Str_MIA_ANG_ZLoc | 40.81 | FanBase_Str_Inertia_Plate_X_Hole_Eng_Hole_Dia | 0.152
FAN_BH_NOM | 0.5 |  | MTRBS_F | 6 | PLTS4_SL2 | 9.1875 | FanBase_Str_DOA_INT_MTR_CHAN_ZLoc | 46.695 | LIA Angle Data |  | FanBase_Str_Inertia_Plate_X_Hole_Clr_Hole_Dia | 0.218
FAN_DC | 24.5 |  | MTRBS_AO | 8 |  |  | FanBase_Str_DOA_INT_FAN_CHAN_XLoc | 22.75 | FanBase_Str_LIA_ANG_Lookup | Angle430.375 | FanBase_Str_Inertia_Plate_X_Hole_Ind_Hole_Dia | 0.125
FAN_DD | 30.25 |  | MTRBS_AR | 9.25 | Parameter | Value | FanBase_Str_DOA_INT_FAN_CHAN_ZLoc | 46.695 | FanBase_Str_LIA_ANG_L | 74.63 | FanBase_Str_Inertia_Plate_X_Hole1_PlateBeside_Btm_Suppresion | 0
FAN_DE | 14.75 |  | MTRBS_AU | 0.75 | Isolator Data |  | FanBase_Str_DOA_INT_CHAN_Lookup | Channel68.2 | FanBase_Str_LIA_ANG_H | 4 | FanBase_Str_Inertia_Plate_X_Hole1_Suppresion | 0
FAN_DX | 1.5 |  | MTRBS_BT | 5.25 | Standard_Isolator_Operating_Height | 7.25 | FanBase_Str_DOA_INT_CHAN_L | 47.77 | FanBase_Str_LIA_ANG_D | 3 | FanBase_Str_Inertia_Plate_X_Hole1_XLoc | 2.375
FAN_G | 41 |  | MTRBS_AT | 0.1875 | ISO_S1_PartNumber | 11 | FanBase_Str_DOA_INT_CHAN_H | 6 | FanBase_Str_LIA_ANG_WT | 0.375 | FanBase_Str_Inertia_Plate_X_Hole1_ArrayQty | 2
FAN_GA | 0.126 |  | MTRBS_XC | 2.125 | ISO_S1_OPHGT | 7.25 | FanBase_Str_DOA_INT_CHAN_LBFT | 8.2 | FanBase_Str_LIA_ANG_FTR | 0.5 | FanBase_Str_Inertia_Plate_X_Hole1_ArrayDist | 1.91
FAN_GB | 0.097 |  | MTRBS_DBOLT_D | 0.625 | ISO_S1_BLT | 1.5 | FanBase_Str_DOA_INT_CHAN_D | 1.92 | FanBase_Str_LIA_ANG_LB | 52.8629 | FanBase_Str_Inertia_Plate_X_Hole2_Suppresion | 1
FAN_GC | 20.5 |  | MTRBS_DBOLT_L | 2.5 | ISO_S1_BW | 6 | FanBase_Str_DOA_INT_CHAN_WT | 0.2 | FanBase_Str_LIA_ANG_HoleLoc_Plane | 1.5 | FanBase_Str_Inertia_Plate_X_Hole2_XLoc | 9.035
FAN_H | 47.75 |  | MTRBS_AYBOLT_D | 0.75 | ISO_S1_BL | 7.625 | FanBase_Str_DOA_INT_CHAN_FTR | 0.343 | FanBase_Str_LIA_ANG_ZLoc | 71 | FanBase_Str_Inertia_Plate_X_Hole2_ArrayQty | 0
FAN_HE | 25.75 |  | MTRBS_AYBOLT_L | 9 | ISO_S1_BT | 0.375 | FanBase_Str_DOA_INT_CHAN_LB | 32.6428 | Down Blast Fan Angle Data |  | FanBase_Str_Inertia_Plate_X_Hole2_ArrayDist | 0.27
FAN_HJ | 23.31 |  | MTRBS_LB | 31 | ISO_S1_BHD | 0.875 | FanBase_Str_DOA_INT_FAN_CHAN_HoleLoc_Plane | 1.1304 | FanBase_Str_DB_ANG_Suppresion | 0 | FanBase_Str_Inertia_Plate_X_Hole3_Suppresion | 1
FAN_HN | 31.75 |  | MTRBS_AdjBolt_Loc | 6 | ISO_S1_BHW | 1.125 | FanBase_Str_DOA_INT_MTR_CHAN_HoleLoc_Plane | 1.1304 | FanBase_Str_DB_ANG_Lookup | Angle430.375 | FanBase_Str_Inertia_Plate_X_Hole3_XLoc | 13.515
FAN_J | 26.25 |  | MTRBS_AdjBolt_ArrayQty | 2 | ISO_S1_BHL | 1.125 | DOW Internal Channel Data |  | FanBase_Str_DB_ANG_L | 42.75 | FanBase_Str_Inertia_Plate_X_Hole3_ArrayQty | 2
FAN_P | 32.88 |  | MTRBS_AdjBolt_ArrayDist | 12 | ISO_S1_HL | 6.44 | FanBase_Str_DOW_INT_CHAN_Suppresion | 0 | FanBase_Str_DB_ANG_H | 4 | FanBase_Str_Inertia_Plate_X_Hole3_ArrayDist | 1.91
FAN_Q | 15.81 |  | MTRBS_Bstyle_Suppresion | 1 | ISO_S1_TDBL | 2 | FanBase_Str_DOW_INT_CHAN_XLoc | 47.9518 | FanBase_Str_DB_ANG_D | 3 | FanBase_Str_Inertia_Plate1_ZDim | 12
FAN_SD | 2.4375 |  | MTRBS_Bstyle_Flange_W | 4 | ISO_S1_TDBD | 0.5 | FanBase_Str_DOW_INT_CHAN_ZLoc | 57.221 | FanBase_Str_DB_ANG_WT | 0.375 | FanBase_Str_Inertia_Plate1_XDim | 76.5306
FAN_KSL | 5.5 |  | MTRBS_Bstyle_Block_W | 2 | ISO_S1_ADJBD | 0.625 | FanBase_Str_DOW_INT_CHAN_Lookup | Channel68.2 | FanBase_Str_DB_ANG_FTR | 0.5 | FanBase_Str_Inertia_Plate1_ZLoc | 27.39 | TRUE
FAN_KSW | 0.63 |  | MTRBS_X_Location | 93.35 | ISO_S2_PartNumber | 14 | FanBase_Str_DOW_INT_CHAN_L | 43.0256 | FanBase_Str_DB_ANG_LB | 30.2812 | FanBase_Str_Inertia_Plate1_LB | 0
FAN_KSD | 0.31 |  | MTRBS_Y_Location | 10.49 | ISO_S2_OPHGT | 7.25 | FanBase_Str_DOW_INT_CHAN_H | 6 | FanBase_Str_DB_ANG_HoleLoc_Plane | 1.5 | FanBase_Str_Inertia_Plate2_ZDim | 12
FAN_AH | 1 |  | MTRBS_Z_Location | -15.88 | ISO_S2_BLT | 1.5 | FanBase_Str_DOW_INT_CHAN_LBFT | 8.2 | FanBase_Str_DB_ANG_ZLoc | 58.69 | FanBase_Str_Inertia_Plate2_XDim | 76.5306
FAN_K | 22.75 |  | MTRBS_AdjBoltHeadThickness | 0.5 | ISO_S2_BW | 6 | FanBase_Str_DOW_INT_CHAN_D | 1.92 | DOA Angle Data |  | FanBase_Str_Inertia_Plate2_ZLoc | 39.39
FAN_M | 15.88 |  | MTRBS_BoltHeadDia | 1.083 | ISO_S2_BL | 7.625 | FanBase_Str_DOW_INT_CHAN_WT | 0.2 | FanBase_Str_DOA_ANG_Lookup | Angle640.375 | FanBase_Str_Inertia_Plate2_LB | 0
FAN_N | 1.13 |  | MTRBS_FlatWasherDia | 1.312 | ISO_S2_BT | 0.375 | FanBase_Str_DOW_INT_CHAN_FTR | 0.343 | FanBase_Str_DOA_ANG_L_Calculation (actual) | 49.19 | FanBase_Str_Inertia_Plate3_ZDim | 12
FAN_ND | 4.62 |  | MTRBS_LockWasherDia | 1.079 | ISO_S2_BHD | 0.875 | FanBase_Str_DOW_INT_CHAN_LB | 29.4008 | FanBase_Str_DOA_ANG_L | 53.315 | FanBase_Str_Inertia_Plate3_XDim | 76.5306
FAN_WOD | 36 |  | MTRBS_NutDia | 1.23 | ISO_S2_BHW | 1.125 | Motor Sup Rail Channel Data |  | FanBase_Str_DOA_ANG_H | 6 | FanBase_Str_Inertia_Plate3_ZLoc | 51.39
FAN_WID | 23.4 |  | MTRBS_TOL1 | 0.5 | ISO_S2_BHL | 1.125 | FanBase_Str_MtrSup_CHAN_XLoc | 93.35 | FanBase_Str_DOA_ANG_D | 4 | FanBase_Str_Inertia_Plate3_LB | 0
FAN_WW | 27.7875 |  |  |  | ISO_S2_HL | 6.44 | FanBase_Str_MtrSup_CHAN_ZLoc | -15.88 | FanBase_Str_DOA_ANG_WT | 0.375 | FanBase_Str_Inertia_Plate4_ZDim | 12
FAN_INLET_FLG_W | 1.5 |  | Parameter | Value | ISO_S2_TDBL | 2 | FanBase_Str_MtrSup_CHAN_Lookup | Channel45.4 | FanBase_Str_DOA_ANG_FTR | 0.5 | FanBase_Str_Inertia_Plate4_XDim | 76.5306
FAN_BRG_SUP_W | 3.5 |  | Top Discharge Flange Data |  | ISO_S2_TDBD | 0.5 | FanBase_Str_MtrSup_CHAN_Spacing | 16 | FanBase_Str_DOA_ANG_LB | 54.6479 | FanBase_Str_Inertia_Plate4_ZLoc | 63.39
FAN_BRG_SUP_T | 0.375 |  | TopDischTrans_Fan_Gap | 4 | ISO_S2_ADJBD | 0.625 | FanBase_Str_MtrSup_CHAN_L_Calculation (actual) | 21.25 | FanBase_Str_DOA_ANG_ISO_L_Add | 0 | FanBase_Str_Inertia_Plate4_LB | 0
FAN_BRG_DIA | 3.6562 |  | TopDischTrans_Roof_Overlap | 1.5 | ISO_S3_PartNumber | 12 | FanBase_Str_MtrSup_CHAN_L | 21.25 | FanBase_Str_DOA_ANG_MTRBS_L_Add | 4.125 | FanBase_Str_Inertia_Plate5_ZDim | 12
FAN_BRG_W | 3 |  | TopDischTrans_Roof_Clearance | 0.125 | ISO_S3_OPHGT | 7.25 | FanBase_Str_MtrSup_CHAN_H | 4 | FanBase_Str_DOA_ANG_ZLoc | 45.8425 | FanBase_Str_Inertia_Plate5_XDim | 76.5306
FAN_BRG_H | 3.7812 |  | TopDischTrans_Flex_Clearance | 0.75 | ISO_S3_BLT | 1.5 | FanBase_Str_MtrSup_CHAN_LBFT | 5.4 | DOA Internal Angle Data |  | FanBase_Str_Inertia_Plate5_ZLoc | 39.39
FAN_FRAME_CUT_FIA | 9.75 |  | TopDischTrans_Corner_Clearance | 0.031 | ISO_S3_BW | 6 | FanBase_Str_MtrSup_CHAN_D | 1.584 | FanBase_Str_DOA_INT_ANG_Suppresion | 0 | FanBase_Str_Inertia_Plate5_LB | 0
FAN_FRAME_CUT_LIA | 0.063 |  | TopDischTrans_Y_Loc | 75.156 | ISO_S3_BL | 7.625 | FanBase_Str_MtrSup_CHAN_WT | 0.184 | FanBase_Str_DOA_INT_ANG_RH_Location | 70.72 | FanBase_Str_Inertia_PlateBeside_Btm_ZDim | 12
FAN_FRAME_TOP_Suppresion | 1 |  | TopDischTrans_Z_Loc | 41.285 | ISO_S3_BT | 0.375 | FanBase_Str_MtrSup_CHAN_FTR | 0.296 | FanBase_Str_DOA_INT_ANG_LH_Location | 84.1 | FanBase_Str_Inertia_PlateBeside_Btm_XDim | 76.5306
FAN_BoltHeadDia | 0.649 |  | TopDischTrans_H | 12 | ISO_S3_BHD | 0.875 | FanBase_Str_MtrSup_CHAN_LB | 9.5625 | FanBase_Str_DOA_INT_ANG_Lookup | Angle430.375 | FanBase_Str_Inertia_PlateBeside_Btm_ZLoc | 39.39
FAN_FlatWasherDia | 0.812 |  | TopDischTrans_X | 42.388 | ISO_S3_BHW | 1.125 | FanBase_Str_MtrSup_CHAN_Std_Overhang | 0.25 | FanBase_Str_DOA_INT_ANG_L | 43.19 | FanBase_Str_Inertia_PlateBeside_Btm_LB | 0
FAN_LockWasherDia | 0.683 |  | TopDischTrans_Z | 31.56 | ISO_S3_BHL | 1.125 | FanBase_Str_MtrSup_CHAN_L_Add | 0 | FanBase_Str_DOA_INT_ANG_H | 4 | FanBase_Str_Inertia_PlateBeside_BtmFiller_ZDim | 12
FAN_NutDia | 0.795 |  | TopDischTrans_FIA_LIA_L | 42.5 | ISO_S3_HL | 6.44 | FanBase_Str_MtrSup_CHAN_Overhang_TypeB | 2.4798 | FanBase_Str_DOA_INT_ANG_D | 3 | FanBase_Str_Inertia_PlateBeside_BtmFiller_XDim | 13.32
|  |  | TopDischTrans_RH_LH_L | 31.386 | ISO_S3_TDBL | 2 | FanBase_Str_MtrSup_CHAN_Overhang_TypeC | 0 | FanBase_Str_DOA_INT_ANG_WT | 0.375 | FanBase_Str_Inertia_PlateBeside_BtmFiller_ZLoc | 39.39
Parameter | Value |  | TopDischTrans_Hole1_YLoc_Top | 0.75 | ISO_S3_TDBD | 0.5 | Isolator Support Angle Data |  | FanBase_Str_DOA_INT_ANG_FTR | 0.5 | FanBase_Str_Inertia_PlateBeside_BtmFiller_XLoc | 46.4902
Weldment Model Data |  |  | TopDischTrans_Hole1_YLoc_Btm | 1.375 | ISO_S3_ADJBD | 0.625 | FanBase_Str_IsoSup_ANG_Suppresion | 1 | FanBase_Str_DOA_INT_ANG_LB | 30.5929 | FanBase_Str_Inertia_PlateBeside_BtmFiller_LB | 0
WLDMNT_FIA_LIA_Direction | 2 |  | TopDischTrans_Hole1_ArrayQty | 3 | ISO_S4_PartNumber | 12 | FanBase_Str_IsoSup_ANG_SizeLookup_Designation | 2 | FanBase_Str_DOA_INT_ANG_HoleLoc_Plane | 1.5 | FanBase_Str_Inertia_PlateBeside_BtmInvFiller_ZDim | 12
WLDMNT_Base_THK | 0.25 |  | TopDischTrans_Hole1_ArrayDist | 4.9375 | ISO_S4_OPHGT | 7.25 | FanBase_Str_IsoSup_ANG_Designation_S1_Loc | 2 |  |  | FanBase_Str_Inertia_PlateBeside_BtmInvFiller_XDim | 13.32
WLDMNT_Base_L | 38.5 |  | TopDischTrans_Stiffener_Flng_L | 1.25 | ISO_S4_BLT | 1.5 | FanBase_Str_IsoSup_ANG_S1_Gusset_Suppresion | 0 |  |  | FanBase_Str_Inertia_PlateBeside_BtmInvFiller_ZLoc | 27.39
WLDMNT_Base_W | 50 |  | TopDischTrans_Stiffener_YLoc | 1.375 | ISO_S4_BW | 6 | FanBase_Str_IsoSup_ANG_Designation_S2_Loc | 2 |  |  | FanBase_Str_Inertia_PlateBeside_BtmInvFiller_XLoc | 46.4902
WLDMNT_Base_H | 6 |  | TopDischTrans_Stiffener_ArrayQty | 1 | ISO_S4_BL | 7.625 | FanBase_Str_IsoSup_ANG_S2_Gusset_Suppresion | 0 |  |  | FanBase_Str_Inertia_PlateBeside_BtmInvFiller_LB | 0
WLDMNT_Base4_FIA_FlngD | 3 |  | TopDischTrans_Stiffener_ArrayDist | 6.25 | ISO_S4_BT | 0.375 | FanBase_Str_IsoSup_ANG_Designation_S3_Loc | 2 |  |  | FanBase_Str_Inertia_Rebar_Lookup | Rebar0.5
WLDMNT_Base4_LIA_FlngD | 3 |  | TopDischTrans_Stiffener_FIA_LIA_L | 42.5 | ISO_S4_BHD | 0.875 | FanBase_Str_IsoSup_ANG_S3_Gusset_Suppresion | 0 |  |  | FanBase_Str_Inertia_Rebar_D | 0.5
WLDMNT_Base4_FIA_Loc | 19.25 |  | TopDischTrans_Stiffener_FIA_LIA_Hole1_XLoc | 1.5 | ISO_S4_BHW | 1.125 | FanBase_Str_IsoSup_ANG_Designation_S4_Loc | 2 |  |  | FanBase_Str_Inertia_Rebar_Zone1_Suppresion | 0
WLDMNT_Base4_LIA_Loc | 19.25 |  | TopDischTrans_Stiffener_FIA_LIA_Hole1_ArrayQty | 6 | ISO_S4_BHL | 1.125 | FanBase_Str_IsoSup_ANG_S4_Gusset_Suppresion | 0 |  |  | FanBase_Str_Inertia_Rebar_Zone2_Suppresion | 0
WLDMNT_Base6_DOA_Suppresion | 1 |  | TopDischTrans_Stiffener_FIA_LIA_Hole1_ArrayDist | 7.9 | ISO_S4_HL | 6.44 | FanBase_Str_IsoSup_ANG_H | 4 |  |  | FanBase_Str_Inertia_Rebar_Zone3_Suppresion | 0
WLDMNT_IntRail_DOA_ZLoc | 19.25 |  | TopDischTrans_Stiffener_RH_LH_L | 31.56 | ISO_S4_TDBL | 2 | FanBase_Str_IsoSup_ANG_D | 6 |  |  | FanBase_Str_Inertia_Rebar_Tollerance | 0.125
WLDMNT_IntRail_DOA_XLoc | 5.5556 |  | TopDischTrans_Stiffener_RH_LH_Hole1_ZLoc | 2 | ISO_S4_TDBD | 0.5 | FanBase_Str_IsoSup_ANG_L | 8 |  |  | FanBase_Str_Inertia_Rebar_Spacing | 9
WLDMNT_IntRail_DOA_L | 38.498 |  | TopDischTrans_Stiffener_RH_LH_Hole1_ArrayQty | 5 | ISO_S4_ADJBD | 0.625 | FanBase_Str_IsoSup_ANG_WT | 0.5 |  |  | FanBase_Str_Inertia_Rebar_OffsetFromBtmOfBase | 2
WLDMNT_IntRail_DOA_Base4_BS_Suppresion | 0 |  | TopDischTrans_Stiffener_RH_LH_Hole1_ArrayDist | 6.89 | ISO_TopNut_Plane_Loc | 0.5 | FanBase_Str_IsoSup_ANG_FTR | 0.5 |  |  | FanBase_Str_Inertia_Rebar_YLoc | 4.906
WLDMNT_IntRail_DOA_Base4_BH_Suppresion | 0 |  | TopDischTrans_Eng_Hole_Dia | 0.152 | ISO_Tiedown_Bolt_Head_Dia | 0.866 | FanBase_Str_IsoSup_ANG_HS | 2 |  |  | FanBase_Str_Inertia_Rebar_Zone1_XDim_Hole_Calc | 6.66
WLDMNT_IntRail_DOA_Base4_LH_Suppresion | 0 |  | TopDischTrans_Clr_Hole_Dia | 0.218 | ISO_S1_XLoc | 106.2452 | FanBase_Str_IsoSup_ANG_HL | 1.25 |  |  | FanBase_Str_Inertia_Rebar_Zone1_XDim | 6
WLDMNT_IntRail_DOA_Base4_RH_Suppresion | 0 |  | TopDischTrans_Thk | 0.05601 | ISO_S1_ZLoc | 68.5 | FanBase_Str_IsoSup_ANG_HD1 | 0.625 |  |  | FanBase_Str_Inertia_Rebar_Zone1_XLength | 5.75
WLDMNT_IntRail_DOA_Base6_LH_Suppresion | 1 |  | TopDischTrans_GA | 16 | ISO_S2_XLoc | 106.2452 | FanBase_Str_IsoSup_ANG_HD2 | 0.875 |  |  | FanBase_Str_Inertia_Rebar_Zone1_ZDim | 12
WLDMNT_IntRail_DOA_Base6_RH_Suppresion | 0 |  |  |  | ISO_S2_ZLoc | 24.89 | FanBase_Str_IsoSup_ANG_LB | 10.8 |  |  | FanBase_Str_Inertia_Rebar_Zone1_ZLength | 11.75
WLDMNT_IntRail_DOA_Rail1_XLoc | 4 |  |  |  | ISO_S3_XLoc | 19.2146 | FanBase_Str_IsoSup_ANG_STD_Offset | 1 |  |  | FanBase_Str_Inertia_Rebar_Zone1_XArray_XStart | 4.92
WLDMNT_IntRail_DOA_Rail2_XLoc | 12 |  |  |  | ISO_S3_ZLoc | 68.5 | FanBase_Str_IsoSup_ANG_Offset_S1_Loc | 1 |  |  | FanBase_Str_Inertia_Rebar_Zone1_XArray_ZStart | 46.695
WLDMNT_IntRail_DOA_Rail1_Suppresion | 1 |  |  |  | ISO_S4_XLoc | 19.2146 | FanBase_Str_IsoSup_ANG_Offset_S2_Loc | 1 |  |  | FanBase_Str_Inertia_Rebar_Zone1_XArrayQty | 1
WLDMNT_IntRail_DOA_Rail2_Suppresion | 1 |  |  |  | ISO_S4_ZLoc | 24.89 | FanBase_Str_IsoSup_ANG_Offset_S3_Loc | 1 |  |  | FanBase_Str_Inertia_Rebar_Zone1_XArrayDist | 6
WLDMNT_IntRail_DOA_Rail1_BBH_LIA_Suppresion | 0 | [5 empty] | FanBase_Str_IsoSup_ANG_Offset_S4_Loc | 1 |  |  | FanBase_Str_Inertia_Rebar_Zone1_ZArray_XStart | 3.2
WLDMNT_IntRail_DOA_Rail2_BBH_LIA_Suppresion | 0 | [5 empty] | FanBase_Str_IsoSup_ANG_Overhang | 1.92 |  |  | FanBase_Str_Inertia_Rebar_Zone1_ZArray_ZStart | 43.695
WLDMNT_IntRail_DOA_Rail1_BBH_FIA_Suppresion | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone1_ZArrayQty | 2
WLDMNT_IntRail_DOA_Rail2_BBH_FIA_Suppresion | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone1_ZArrayDist | 6
WLDMNT_IntRail_DOA_Coping_Suppresion | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone1_LB | 0
WLDMNT_IntRail_DOW_ZLoc | -10 | [9 empty] | FanBase_Str_Inertia_Concrete_Zone1_LB | 0
WLDMNT_IntRail_DOW_Zloc_BtmDisch | -1 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_XDim_Hole_Calc | 4.48
WLDMNT_IntRail_DOW_XLoc | -9.5 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_XDim | 6
WLDMNT_IntRail_DOW_L | 28.748 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_XLength | 5.75
WLDMNT_IntRail_DOW_BtmDisch_Base4_Suppresion | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_ZDim | 47.77
WLDMNT_IntRail_DOW_Base4_Suppresion | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_ZLength | 47.52
WLDMNT_IntRail_DOW_Base6_Suppresion | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_XArray_XStart | 9.4
WLDMNT_IsoSupAng_ZLoc | 21.251 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_XArray_ZStart | 46.695
WLDMNT_IsoSupAng_XLoc | 25.001 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_XArrayQty | 1
WLDMNT_MtrRail_L | 17 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_XArrayDist | 6
WLDMNT_MtrRail_Spacing | 12 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_ZArray_XStart | 9.4
WLDMNT_MtrRail_XLoc | 17 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_ZArray_ZStart | 28.695
WLDMNT_MtrRail_ZLoc | -11.25 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_ZArrayQty | 5
WLDMNT_FanHole_Dia | 0.5 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_ZArrayDist | 9
WLDMNT_FanHole_Spacing_Z | 15.4 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone2_LB | 0
WLDMNT_FanHole_Spacing_X | 28.748 | [9 empty] | FanBase_Str_Inertia_Concrete_Zone2_LB | 0
WLDMNT_FanHole_XLoc | -9.5 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_XDim_Hole_Calc | 6.66
WLDMNT_FanHole_ZLoc | 6.55 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_XDim | 6
WLDMNT_FanHole_6_RHSuppresion_BH | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_XLength | 5.75
WLDMNT_FanHole_6_RHSuppresion_BS | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_ZDim | 47.77
WLDMNT_FanHole_6_LHSuppresion_BH | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_ZLength | 47.52
WLDMNT_FanHole_6_LHSuppresion_BS | 1 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_XArray_XStart | 15.6
WLDMNT_FanHole_6_RHSuppresion_BBH | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_XArray_ZStart | 46.695
WLDMNT_FanHole_6_RHSuppresion_BBS | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_XArrayQty | 1
WLDMNT_FanHole_6_LHSuppresion_BBH | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_XArrayDist | 6
WLDMNT_FanHole_6_LHSuppresion_BBS | 0 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_ZArray_XStart | 15.6
WLDMNT_MtrBaseHole_Dia | 0.75 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_ZArray_ZStart | 28.695
WLDMNT_MtrBaseHole_Spacing_Z | 12 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_ZArrayQty | 5
WLDMNT_MtrBaseHole_Spacing_X | 15 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_ZArrayDist | 9
WLDMNT_MtrBaseHole_XLoc | 17 | [9 empty] | FanBase_Str_Inertia_Rebar_Zone3_LB | 0
WLDMNT_MtrBaseHole_ZLoc | -11.25 | [9 empty] | FanBase_Str_Inertia_Concrete_Zone3_LB | 0
WLDMNT_MtrBaseHole_4_RHSuppresion_BH | 0
WLDMNT_MtrBaseHole_4_RHSuppresion_BS | 0
WLDMNT_MtrBaseHole_4_LHSuppresion_BH | 0
WLDMNT_MtrBaseHole_4_LHSuppresion_BS | 0
WLDMNT_MtrBaseHole_6_RHSuppresion_BH | 0
WLDMNT_MtrBaseHole_6_RHSuppresion_BS | 0
WLDMNT_MtrBaseHole_6_LHSuppresion_BH | 0
WLDMNT_MtrBaseHole_6_LHSuppresion_BS | 1
WLDMNT_IsoHole_ZLoc | 17.251
WLDMNT_IsoHole_XLoc | 29.75
WLDMNT_ISOX | 87.03
WLDMNT_ISOZ | 43.61
WLDMNT_D1 | 51.61
WLDMNT_D2 | 77.53
WLDMNT_D3 | 45.5 | int doa rail1
WLDMNT_D4 | 62.56 | int doa rail2
WLDMNT_D5 | - | int 4" dow mtr rail
WLDMNT_D6 | - | int btm disch dow rail
WLDMNT_D7 | - | fia dow rail loc
WLDMNT_D8 | - | lia dow rail loc
WLDMNT_D9 | 1.92 | mtr sup rail zloc
WLDMNT_D10 | 16 | mtr sup rail zspcg
WLDMNT_D11 | 2.48 | mtr sup rail mtr side overhang
WLDMNT_F1 | 1.13 | fan dow hole loc rh
WLDMNT_F2 | 45.5 | fan dow hole spcg
WLDMNT_F3 | 30.9 | fan dow hole loc lh
WLDMNT_F4 | 11.92 | fan doa hole loc fia
WLDMNT_F5 | 31.76 | fan doa hole loc lia
WLDMNT_F6 | 7.93 | fan doa hole spcg
WLDMNT_MB1 | 1.38 | mtrbs dow hole loc rh
WLDMNT_MB2 | 18.5 | mtrbs dow hole spcg
WLDMNT_MB3 | 1.37 | mtrbs dow hole loc lh
WLDMNT_MB4 | 2 | mtrbs doa fia hole loc
WLDMNT_MB5 | 16 | mtrbs doa hole spcg
WLDMNT_MB6 | - | mtrbs doa lia hole loc

## Fan Data
| Twin City BAE DWDI Fan Data (Horizontal Discharge) | [26 empty] | Key Slot Dimensions |  |  | Isolator Location Dimensions |  |  |  |  | Wheel Data Dimensions |  |  |  | Bearing Data Dimensions |  |  |  |  | Class 1 & 2 fans | [36 empty] | Class 3 fans
| FAN | WH_DIA_Nominal | MIN_T_FRAME | MAX_T_FRAME | FAN_A | FAN_B | FAN_BAH | FAN_BAW | FAN_BAT | FAN_BH | FAN_BH_NOM | FAN_DC | FAN_DD | FAN_DE | FAN_DX | FAN_G | FAN_GA | FAN_GB | FAN_GC | FAN_H | FAN_HE | FAN_HJ | FAN_HN | FAN_J | FAN_P | FAN_Q | FAN_SD | FAN_KSL | FAN_KSW | FAN_KSD | FAN_AH (DB Fans Only) | FAN_K | FAN_M | FAN_N | FAN_ND | FAN_WOD | FAN_WID | FAN_WW | FAN_INLET_FLG_W | FAN_BRG_SUP_W | FAN_BRG_SUP_T | FAN_BRG_DIA | FAN_BRG_W | FAN_BRG_H | FAN_MAX_T_FRAME_CL1 | FAN_MAX_T_FRAME_CL2 | FAN_A_CL1/CL2 | FAN_B_CL1/CL2 | FAN_BAH_CL1/CL2 | FAN_BAW_CL1/CL2 | FAN_BAT_CL1/CL2 | FAN_BH_CL1/CL2 | FAN_DC_T_CL1/CL2 | FAN_DC_B_CL1/CL2 | FAN_DX_CL1/CL2 | FAN_G_CL1/CL2 | FAN_GA_CL1/CL2 | FAN_GB_CL1/CL2 | FAN_GC_CL1/CL2 | FAN_H_CL1/CL2 | FAN_HE_CL1/CL2 | FAN_HJ_CL1/CL2 | FAN_HN_T_CL1/CL2 | FAN_HN_B_CL1/CL2 | FAN_J_CL1 | FAN_J_CL2 | FAN_K_CL1/CL2 | FAN_KSL_CL1/CL2 | FAN_KSW_CL1 | FAN_KSW_CL2 | FAN_KSD_CL1 | FAN_KSD_CL2 | FAN_M_CL1/CL2 | FAN_N_CL1/CL2 | FAN_P_CL1 | FAN_P_CL2 | FAN_Q_CL1/CL2 | FAN_SD_CL1 | FAN_SD_CL2 | FAN_BRG_SUP_W_CL1 | FAN_BRG_SUP_W_CL2 | FAN_MAX_T_FRAME_CL3 | FAN_A_CL3 | FAN_B_CL3 | FAN_BAH_CL3 | FAN_BAW_CL3 | FAN_BAT_CL3 | FAN_BH_CL3 | FAN_DC_T_CL3 | FAN_DC_B_CL3 | FAN_DX_CL3 | FAN_G_CL3 | FAN_GA_CL3 | FAN_GB_CL3 | FAN_GC_CL3 | FAN_H_CL3 | FAN_HE_CL3 | FAN_HJ_CL3 | FAN_HN_T_CL3 | FAN_HN_B_CL3 | FAN_J_CL3 | FAN_K_CL3 | FAN_KSL_CL3 | FAN_KSW_CL3 | FAN_KSD_CL3 | FAN_M_CL3 | FAN_N_CL3 | FAN_P_CL3 | FAN_Q_CL3 | FAN_SD_CL3 | FAN_BRG_SUP_W_CL3
TYPE A | 122H | 12.2 | 143T | 254T | 13 | 17.5 | 1.5 | 1.5 | 0.188 | 0.44 | 0.375 | 10.25 | 11.44 | 5.19 | 1 | 18.5 | 0.07 | 0.07 | 9.875 | 20.5 | 10.56 | 9.25 | 12.94 | 12.38 | 16.25 | 6.44 | 1.4375 | 3 | 0.38 | 0.19 | n/a | 9.63 | 6.75 | 0.63 | 3.125 | 15.5 | 9.516 | 11.375 | 1.25 | 2.5 | 0.375 | 2.1562 | 2 | 2.2812 | 213T | 254T | 13 | 17.5 | 1.5 | 1.5 | 0.188 | 0.44 | 10.25 | 15 | 1 | 18.5 | 0.07 | 0.07 | 9.875 | 20.5 | 10.56 | 9.25 | 12.94 | 9.31 | 11.44 | 12.38 | 9.63 | 3 | 0.25 | 0.38 | 0.13 | 0.19 | 6.75 | 0.63 | 15.25 | 16.25 | 6.44 | 1.1875 | 1.4375 | 2.5 | 2.5 | 254T | 13.13 | 17.63 | 1.5 | 2 | 0.188 | 0.44 | 10.25 | 15.5 | 1.25 | 18.63 | 0.126 | 0.126 | 9.875 | 21.63 | 10.63 | 9.75 | 13 | 9.38 | 12.56 | 9.94 | 3.5 | 0.5 | 0.25 | 6.5 | 0.88 | 17.06 | 6.44 | 1.9375 | 3
| 135H | 13.5 | 143T | 254T | 14.31 | 19.5 | 1.5 | 1.5 | 0.188 | 0.44 | 0.375 | 11.25 | 12.75 | 5.875 | 1 | 19.75 | 0.07 | 0.07 | 10.5 | 22.5 | 11.63 | 10.25 | 14.25 | 13.38 | 17.25 | 7.13 | 1.6875 | 3 | 3.8 | 0.19 | n/a | 10.63 | 7.38 | 0.63 | 3.12 | 16.75 | 10.53 | 12.675 | 1.25 | 2.5 | 0.375 | 2.5312 | 2 | 2.6562 | 213T | 254T | 14.31 | 19.5 | 1.5 | 1.5 | 0.188 | 0.44 | 11.25 | 16.25 | 1 | 19.75 | 0.07 | 0.07 | 10.5 | 22.5 | 11.63 | 10.25 | 14.25 | 10.25 | 12.44 | 13.38 | 10.63 | 3 | 0.25 | 3.8 | 0.13 | 0.19 | 7.38 | 0.63 | 16.25 | 17.25 | 7.13 | 1.1875 | 1.6875 | 2.5 | 2.5 | 254T | 14.44 | 19.63 | 1.5 | 2 | 0.188 | 0.44 | 11.25 | 16.75 | 1.25 | 19.88 | 0.126 | 0.126 | 10.5 | 23.63 | 11.69 | 10.75 | 14.31 | 10.31 | 13.56 | 10.94 | 4 | 0.5 | 0.25 | 7.13 | 0.88 | 18.56 | 7.13 | 1.9375 | 3
| 150H | 15 | 143T | 256T | 15.88 | 21.5 | 1.5 | 1.5 | 0.188 | 0.44 | 0.375 | 12.25 | 14.31 | 6.56 | 1 | 21.5 | 0.07 | 0.07 | 11.375 | 24.5 | 12.88 | 11.44 | 15.81 | 14.38 | 18.75 | 7.88 | 1.6875 | 3.5 | 0.38 | 0.19 | n/a | 11.63 | 8.25 | 0.63 | 3.125 | 18.5 | 11.7 | 13.975 | 1.25 | 2.5 | 0.375 | 2.5312 | 2 | 2.6562 | 215T | 256T | 15.88 | 21.5 | 1.5 | 1.5 | 0.188 | 0.44 | 12.25 | 18 | 1 | 21.5 | 0.07 | 0.07 | 11.375 | 24.5 | 12.88 | 11.44 | 15.81 | 11.38 | 14.38 | 14.38 | 11.63 | 3.5 | 0.38 | 0.38 | 0.19 | 0.19 | 8.25 | 0.63 | 18.75 | 18.75 | 7.88 | 1.4375 | 1.6875 | 2.5 | 2.5 | 256T | 16 | 21.63 | 1.5 | 2 | 0.188 | 0.44 | 12.25 | 18.5 | 1.25 | 21.63 | 0.126 | 0.126 | 11.375 | 25.63 | 12.94 | 11.94 | 15.88 | 11.44 | 15.13 | 11.94 | 4 | 0.5 | 0.25 | 8 | 0.88 | 20.13 | 7.88 | 2.1875 | 3.5
| 165H | 16.5 | 143T | 256T | 17.44 | 23.625 | 1.5 | 2 | 0.188 | 0.44 | 0.375 | 13.5 | 15.88 | 6.755 | 1 | 24.25 | 0.07 | 0.07 | 12.125 | 27.625 | 14.13 | 12.63 | 17.38 | 15.56 | 20.06 | 8.69 | 1.9375 | 3.5 | 0.5 | 0.25 | n/a | 12.94 | 8.75 | 0.88 | 3.375 | 21.25 | 12.87 | 15.3563 | 1.25 | 3 | 0.375 | 2.9062 | 2.5 | 3.0312 | 215T | 256T | 17.44 | 23.625 | 1.5 | 2 | 0.188 | 0.44 | 13.5 | 19.5 | 1 | 24.25 | 0.07 | 0.07 | 12.125 | 27.625 | 14.13 | 12.63 | 17.38 | 12.5 | 15.44 | 15.56 | 12.94 | 3.5 | 0.38 | 0.5 | 0.19 | 0.25 | 8.75 | 0.88 | 19.81 | 20.06 | 8.69 | 1.4375 | 1.9375 | 2.5 | 3 | 256T | 17.56 | 23.75 | 1.5 | 2 | 0.188 | 0.44 | 13.5 | 19.5 | 1.25 | 23.13 | 0.126 | 0.126 | 12.125 | 27.75 | 14.19 | 13.13 | 17.44 | 12.56 | 16.19 | 13 | 4.5 | 0.5 | 0.25 | 8.75 | 0.88 | 21.69 | 8.69 | 2.1875 | 3.5
| 182H | 18.2 | 145T | 286T | 19.38 | 26 | 1.5 | 2 | 0.188 | 0.44 | 0.375 | 14.75 | 17.81 | 7.81 | 1.25 | 26 | 0.097 | 0.07 | 13 | 30 | 15.69 | 14 | 19.31 | 16.75 | 21.75 | 9.63 | 1.9375 | 4 | 0.5 | 0.25 | n/a | 14.13 | 9.63 | 0.88 | 3.37 | 23 | 14.196 | 16.9 | 1.25 | 3 | 0.375 | 2.9062 | 2.5 | 3.0312 | 254T | 286T | 19.38 | 26 | 1.5 | 2 | 0.188 | 0.44 | 14.75 | 21.5 | 1.25 | 26 | 0.097 | 0.07 | 13 | 30 | 15.69 | 14 | 19.31 | 13.81 | 16.63 | 16.75 | 14.13 | 4 | 0.38 | 0.5 | 0.19 | 0.25 | 9.63 | 0.88 | 21.5 | 21.75 | 9.63 | 1.6875 | 1.9375 | 2.5 | 3 | 284T | 19.5 | 26.13 | 2 | 2 | 0.25 | 0.56 | 14.75 | 22 | 1.25 | 27 | 0.126 | 0.126 | 13.5 | 30.13 | 15.75 | 14.5 | 19.38 | 13.88 | 17.38 | 14.19 | 4.5 | 0.5 | 0.25 | 9.63 | 0.88 | 22.88 | 9.63 | 2.1875 | 3.5
| 200H | 20 | 145T | 286T | 21.19 | 28.5 | 1.5 | 2 | 0.188 | 0.56 | 0.5 | 16.25 | 19.63 | 8.63 | 1.25 | 28 | 0.097 | 0.07 | 14 | 32.5 | 17.31 | 15.31 | 21.13 | 18.56 | 23.56 | 10.56 | 2.1875 | 4 | 0.5 | 0.25 | n/a | 15.38 | 10.63 | 0.88 | 3.37 | 25 | 15.6 | 18.525 | 1.25 | 3.5 | 0.375 | 3.2812 | 3 | 3.4062 | 254T | 286T | 21.19 | 28.5 | 1.5 | 2 | 0.188 | 0.56 | 16.25 | 23.5 | 1.25 | 28 | 0.097 | 0.07 | 14 | 32.5 | 17.31 | 15.31 | 21.13 | 15.19 | 17.88 | 18.56 | 15.38 | 4 | 0.38 | 0.5 | 0.19 | 0.25 | 10.63 | 0.88 | 22.75 | 23.56 | 10.56 | 1.6875 | 2.1875 | 2.5 | 3.5 | 286T | 21.31 | 28.63 | 2 | 2 | 0.25 | 0.56 | 16.25 | 24 | 1.25 | 29 | 0.126 | 0.126 | 14.5 | 32.63 | 17.38 | 15.81 | 21.19 | 15.25 | 19.13 | 15.44 | 5 | 0.63 | 0.31 | 10.63 | 0.88 | 25.25 | 10.56 | 2.4375 | 3.5
| 222H | 22.2 | 145T | 324T | 23.56 | 31.625 | 2 | 2 | 0.25 | 0.56 | 0.5 | 18 | 22 | 10.375 | 1.25 | 31.25 | 0.097 | 0.07 | 15.625 | 35.625 | 19.06 | 17.19 | 23.5 | 20.63 | 26.25 | 11.75 | 2.4375 | 4.5 | 0.63 | 0.31 | n/a | 16.94 | 11.75 | 0.88 | 3.875 | 27.25 | 17.316 | 20.5563 | 1.25 | 3.5 | 0.375 | 3.6562 | 3 | 3.7812 | 256T | 324T | 23.56 | 31.625 | 2 | 2 | 0.25 | 0.56 | 18 | 26 | 1.25 | 31.25 | 0.097 | 0.07 | 15.625 | 35.625 | 19.06 | 17.19 | 23.5 | 16.81 | 19.56 | 20.63 | 16.94 | 4.5 | 0.5 | 0.63 | 0.25 | 0.31 | 11.75 | 0.88 | 25.06 | 26.25 | 11.75 | 1.9375 | 2.4375 | 3 | 3.5 | 324T | 23.69 | 31.75 | 2.5 | 2.5 | 0.25 | 0.56 | 18 | 26.5 | 1.25 | 32.25 | 0.126 | 0.126 | 16.125 | 36.75 | 19.13 | 17.69 | 23.56 | 16.88 | 20.69 | 17.25 | 5 | 0.63 | 0.31 | 11.5 | 1.13 | 26.81 | 11.75 | 2.4375 | 3.5
TYPE B | 245H | 24.5 | 143T | 326T | 25.94 | 34.875 | 2 | 2 | 0.25 | 0.56 | 0.5 | 20 | 24.38 | 11.63 | 1.25 | 33.5 | 0.097 | 0.07 | 16.75 | 38.875 | 21 | 19 | 25.88 | 22.31 | 28.44 | 12.94 | 2.4375 | 5 | 0.63 | 0.31 | n/a | 18.56 | 12.88 | 0.88 | 3.87 | 29.5 | 19.11 | 22.6687 | 1.5 | 3.5 | 0.375 | 3.6562 | 3 | 3.7812 | 284T | 326T | 25.94 | 34.875 | 2 | 2 | 0.25 | 0.56 | 20 | 28.25 | 1.25 | 33.5 | 0.097 | 0.07 | 16.75 | 38.875 | 21 | 19 | 25.88 | 18.5 | 21.81 | 22.31 | 18.56 | 5 | 0.5 | 0.63 | 0.25 | 0.31 | 12.88 | 0.88 | 27.81 | 28.44 | 12.94 | 2.1875 | 2.4375 | 3.5 | 3.5 | 326T | 26.19 | 35 | 2.5 | 2.5 | 0.25 | 0.56 | 20 | 28.75 | 1.5 | 34.5 | 0.175 | 0.175 | 17.25 | 40 | 21.13 | 19.5 | 26 | 18.63 | 22.38 | 18.88 | 6 | 0.63 | 0.31 | 12.63 | 1.13 | 29.5 | 12.94 | 2.4375 | 3.5
| 270H | 27 | 145T | 326T | 28.63 | 38.25 | 2 | 2 | 0.25 | 0.56 | 0.5 | 22 | 27.06 | 13.06 | 1.5 | 36 | 0.097 | 0.07 | 18 | 42.25 | 23.19 | 20.94 | 28.56 | 24.31 | 30.44 | 14.25 | 2.6875 | 5 | 0.63 | 0.31 | n/a | 20.25 | 14.13 | 0.88 | 3.87 | 32 | 21.06 | 24.8625 | 1.5 | 4 | 0.5 | 4.0312 | 3.5 | 4.1562 | 284T | 326T | 28.63 | 38.25 | 2 | 2 | 0.25 | 0.56 | 22 | 31 | 1.5 | 36 | 0.097 | 0.07 | 18 | 42.25 | 23.19 | 20.94 | 28.56 | 20.44 | 23.5 | 24.31 | 20.25 | 5 | 0.5 | 0.63 | 0.25 | 0.31 | 14.13 | 0.88 | 29.5 | 30.44 | 14.25 | 2.1875 | 2.6875 | 3.5 | 4 | 326T | 28.88 | 38.5 | 2.5 | 2.5 | 0.25 | 0.56 | 22 | 31.5 | 1.5 | 37 | 0.175 | 0.175 | 18.5 | 43.5 | 23.31 | 21.44 | 28.69 | 20.56 | 24.44 | 20.63 | 6 | 0.63 | 0.31 | 13.88 | 1.13 | 31.56 | 14.25 | 2.6875 | 4
| 300H | 30 | 143T | 364T | 31.81 | 42.75 | 2.5 | 2.5 | 0.25 | 0.56 | 0.5 | 24.5 | 30.25 | 14.75 | 1.5 | 41 | 0.126 | 0.097 | 20.5 | 47.75 | 25.75 | 23.31 | 31.75 | 26.25 | 32.88 | 15.81 | 2.4375 | 5.5 | 0.63 | 0.31 | n/a | 22.75 | 15.88 | 1.13 | 4.62 | 36 | 23.4 | 27.7875 | 1.5 | 3.5 | 0.375 | 3.6562 | 3 | 3.7812 | 286T | 364T | 31.81 | 42.75 | 2.5 | 2.5 | 0.25 | 0.56 | 24.5 | 34.25 | 1.5 | 41 | 0.126 | 0.097 | 20.5 | 47.75 | 25.75 | 23.31 | 31.75 | 22.75 | 26.25 | 26.25 | 22.75 | 5.5 | 0.63 | 0.63 | 0.31 | 0.31 | 15.88 | 1.13 | 32.88 | 32.88 | 15.81 | 2.4375 | 2.4375 | 3.5 | 3.5 | 364T | 32 | 42.88 | 3 | 3 | 0.313 | 0.81 | 24.5 | 34.75 | 1.5 | 42 | 0.175 | 0.175 | 21 | 48.88 | 25.81 | 23.81 | 31.81 | 22.81 | 26.63 | 23.06 | 7 | 0.63 | 0.31 | 15.63 | 1.38 | 34.75 | 15.81 | 2.6875 | 4
| 330H | 33 | 143T | 365T | 35.13 | 46.75 | 2.5 | 2.5 | 0.25 | 0.56 | 0.5 | 27 | 33.56 | 16.56 | 1.5 | 44 | 0.126 | 0.097 | 22 | 51.75 | 28.38 | 25.75 | 35.06 | 28.25 | 34.88 | 17.5 | 2.4375 | 5.5 | 0.63 | 0.31 | n/a | 24.75 | 17.38 | 1.13 | 4.62 | 39 | 25.74 | 30.3875 | 1.5 | 4 | 0.5 | 3.6562 | 3.5 | 3.7812 | 324T | 365T | 35.13 | 46.75 | 2.5 | 2.5 | 0.25 | 0.56 | 27 | 37.25 | 1.5 | 44 | 0.126 | 0.097 | 22 | 51.75 | 28.38 | 25.75 | 35.06 | 25 | 28.25 | 28.25 | 24.75 | 5.5 | 0.63 | 0.63 | 0.31 | 0.31 | 17.38 | 1.13 | 34.88 | 34.88 | 17.5 | 2.4375 | 2.4375 | 3.5 | 4 | 365T | 35.31 | 46.88 | 3 | 3 | 0.313 | 0.81 | 27 | 37.75 | 1.5 | 45 | 0.175 | 0.175 | 22.5 | 52.88 | 28.44 | 26.25 | 35.13 | 25.06 | 28.44 | 25.06 | 7 | 0.75 | 0.38 | 17.13 | 1.38 | 36.69 | 17.5 | 2.9375 | 4
| 365H | 36.5 | 143T | 404T | 38.69 | 51.875 | 2.5 | 2.5 | 0.25 | 0.56 | 0.5 | 29.5 | 37.13 | 18.13 | 1.5 | 48 | 0.126 | 0.097 | 24 | 56.875 | 31.5 | 28.5 | 38.63 | 31.13 | 37.75 | 19.25 | 2.6875 | 5.5 | 0.63 | 0.31 | n/a | 27.31 | 18.88 | 1.13 | 5.12 | 43 | 28.47 | 33.7188 | 1.5 | 4 | 0.5 | 4.0312 | 3.5 | 4.1562 | 324T | 404T | 38.69 | 51.875 | 2.5 | 2.5 | 0.25 | 0.56 | 29.5 | 41 | 1.5 | 48 | 0.126 | 0.097 | 24 | 56.875 | 31.5 | 28.5 | 38.63 | 27.75 | 31.13 | 31.13 | 27.31 | 5.5 | 0.63 | 0.63 | 0.31 | 0.31 | 18.88 | 1.13 | 37.75 | 37.75 | 19.25 | 2.6875 | 2.6875 | 4 | 4 | 404T | 38.88 | 52 | 3 | 3 | 0.313 | 0.81 | 29.5 | 41.5 | 1.5 | 49 | 0.175 | 0.175 | 24.5 | 58 | 31.56 | 29 | 38.69 | 27.81 | 31 | 27.63 | 7 | 0.75 | 0.38 | 18.63 | 1.38 | 39.25 | 19.25 | 2.9375 | 5
TYPE C | 402H | 40.2 | 145T | 404T | 42.63 | 57.25 | 3 | 3 | 0.313 | 0.81 | 0.75 | 33 | 41.06 | 20.81 | 1.5 | 52.5 | 0.126 | 0.097 | 26.25 | 63.25 | 34.69 | 31.5 | 42.56 | 33.81 | 40.94 | 21.25 | 2.6875 | 6 | 0.63 | 0.31 | n/a | 30.25 | 20.88 | 1.38 | 5.37 | 46.5 | 31.356 | 37.2125 | 1.75 | 4 | 0.5 | 4.0312 | 3.5 | 4.1562 | 326T | 404T | 42.63 | 57.25 | 3 | 3 | 0.313 | 0.81 | 33 | 45.5 | 1.5 | 52.5 | 0.126 | 0.097 | 26.25 | 63.25 | 34.69 | 31.5 | 42.56 | 30.56 | 33.5 | 33.81 | 30.25 | 6 | 0.63 | 0.63 | 0.31 | 0.31 | 20.88 | 1.38 | 40.63 | 40.94 | 21.25 | 2.4375 | 2.6875 | 4 | 4 | 404T | 42.81 | 57.38 | 3 | 4 | 0.313 | 0.81 | 33 | 45.5 | 2 | 52.5 | 0.175 | 0.175 | 26.25 | 65.38 | 34.75 | 32 | 42.63 | 30.63 | 35.06 | 30.81 | 8 | 0.88 | 0.44 | 20.38 | 1.88 | 44.38 | 21.25 | 3.4375 | 5
| 445H | 44.5 | 182T | 405T | 47.13 | 63.125 | 3 | 3 | 0.313 | 0.81 | 0.75 | 35.5 | 45.56 | 23.31 | 1.5 | 56.5 | 0.126 | 0.097 | 28.25 | 69.125 | 38.25 | 34.88 | 47.06 | 36.56 | 43.81 | 23.5 | 2.9375 | 6 | 0.75 | 0.38 | n/a | 33.19 | 22.88 | 1.38 | 5.37 | 50.5 | 34.71 | 41.0312 | 1.75 | 5 | 0.5 | 4.4062 | 4.5 | 4.5312 | 364T | 405T | 47.13 | 63.125 | 3 | 3 | 0.313 | 0.81 | 35.5 | 50 | 1.5 | 56.5 | 0.126 | 0.097 | 28.25 | 69.125 | 38.25 | 34.88 | 47.06 | 33.75 | 36.44 | 36.56 | 33.19 | 6 | 0.63 | 0.75 | 0.31 | 0.38 | 22.88 | 1.38 | 43.56 | 43.81 | 23.5 | 2.4375 | 2.9375 | 4 | 5 | 405T | 47.31 | 63.25 | 3 | 4 | 0.313 | 0.81 | 35.5 | 50 | 2 | 56.5 | 0.175 | 0.175 | 28.25 | 71.25 | 38.31 | 35.38 | 47.13 | 33.81 | 38 | 33.75 | 8 | 0.88 | 0.44 | 22.38 | 1.88 | 47.31 | 23.5 | 3.4375 | 5
| 490H | 49 | 182T | 445T | 51.94 | 69.5 | 3 | 3 | 0.313 | 0.81 | 0.75 | 39 | 50.38 | 25.63 | 2 | 61.5 | 0.126 | 0.097 | 30.75 | 75.5 | 42.19 | 38.5 | 51.88 | 41.13 | 49.44 | 25.88 | 3.4375 | 7 | 0.88 | 0.44 | n/a | 36.38 | 25.38 | 1.38 | 5.37 | 55.5 | 38.22 | 45.175 | 1.75 | 5 | 0.5 | 5.1562 | 4.5 | 5.2812 | 365T | 445T | 51.94 | 69.5 | 3 | 3 | 0.313 | 0.81 | 39 | 54.75 | 2 | 61.5 | 0.126 | 0.097 | 30.75 | 75.5 | 42.19 | 38.5 | 51.88 | 37.19 | 39.94 | 41.13 | 36.38 | 7 | 0.63 | 0.88 | 0.31 | 0.44 | 25.38 | 1.38 | 48.06 | 49.44 | 25.88 | 2.6875 | 3.4375 | 4 | 5 | 445T | 52.13 | 69.63 | 3 | 4 | 0.313 | 0.81 | 39 | 54.75 | 2 | 61.5 | 0.175 | 0.175 | 30.75 | 77.63 | 42.25 | 39 | 51.94 | 37.25 | 41.94 | 36.94 | 9 | 1 | 0.5 | 24.88 | 1.88 | 52.31 | 25.88 | 3.9375 | 6
| 542H | 54.2 | 254T | 445T | 57.38 | 77 | 3 | 4 | 0.313 | 0.81 | 0.75 | 43.5 | 55.81 | 28.31 | 2 | 67 | 0.126 | 0.097 | 33.5 | 85 | 46.69 | 42.56 | 57.31 | 44.19 | 51.5 | 28.63 | 3.4375 | 6 | 0.88 | 0.44 | n/a | 40.63 | 27.63 | 1.88 | 5.87 | 61 | 42.276 | 50.05 | 1.75 | 5 | 0.5 | 5.1562 | 4.5 | 5.2812 | 404T | 445T | 57.38 | 77 | 3 | 4 | 0.313 | 0.81 | 43.5 | 60.25 | 2 | 67 | 0.126 | 0.097 | 33.5 | 85 | 46.69 | 42.56 | 57.31 | 41.19 | 43.75 | 44.19 | 40.63 | 6 | 0.75 | 0.88 | 0.38 | 0.44 | 27.63 | 1.88 | 51 | 51.5 | 28.63 | 2.9375 | 3.4375 | 4 | 5 | 445T | 57.56 | 77.13 | 3.5 | 5 | 0.5 | 0.81 | 43.5 | 60.75 | 2.5 | 67 | 0.175 | 0.175 | 33.5 | 87.13 | 46.75 | 43.06 | 57.38 | 41.25 | 45.69 | 41.19 | 9 | 1 | 0.5 | 27.13 | 2.38 | 56.06 | 28.63 | 3.9375 | 6
| 600H | 60 | 254T | 445T | 63.5 | 85 | 3 | 4 | 0.313 | 0.81 | 0.75 | 48 | 61.94 | 31.44 | 2 | 73 | 0.126 | 0.097 | 36.5 | 93 | 51.69 | 47.19 | 63.44 | 49.63 | 59 | 31.69 | 3.9375 | 8 | 1 | 0.5 | n/a | 44.63 | 30.63 | 1.88 | 5.87 | 67 | 46.8 | 55.25 | 2 | 6 | 0.5 | 5.9062 | 5.5 | 6.0312 | 405T | 445T | 63.5 | 85 | 3 | 4 | 0.313 | 0.81 | 48 | 66.25 | 2 | 73 | 0.126 | 0.097 | 36.5 | 93 | 51.69 | 47.19 | 63.44 | 45.56 | 48.88 | 49.63 | 44.63 | 8 | 0.88 | 1 | 0.44 | 0.5 | 30.63 | 1.88 | 58.19 | 59 | 31.69 | 3.4375 | 3.9375 | 5 | 6 | 445T | 63.69 | 85.13 | 3.5 | 5 | 0.5 | 0.81 | 48 | 66.75 | 2.5 | 74 | 0.175 | 0.175 | 37 | 95.13 | 51.75 | 47.69 | 63.5 | 45.63 | 50.44 | 45.19 | 9.5 | 1 | 0.5 | 30.13 | 2.38 | 61.31 | 31.69 | 4.4375 | 7
| 660H | 66 | 254T | 445T | 69.69 | 93.75 | 3.5 | 5 | 0.5 | 0.81 | 0.75 | 52.5 | 68.13 | 35.13 | 2.5 | 80 | 0.126 | 0.097 | 40 | 103.75 | 56.81 | 51.94 | 69.63 | 54.06 | 63.38 | 34.75 | 3.9375 | 8 | 1 | 0.5 | n/a | 49.5 | 33.13 | 2.38 | 6.87 | 73 | 51.48 | 60.9375 | 2 | 6 | 0.5 | 5.9062 | 5.5 | 6.0312 | 405T | 445T | 69.69 | 93.75 | 3.5 | 5 | 0.5 | 0.81 | 52.5 | 73.25 | 2.5 | 80 | 0.126 | 0.097 | 40 | 103.75 | 56.81 | 51.94 | 69.63 | 49.94 | 53.25 | 54.06 | 49.5 | 8 | 0.88 | 1 | 0.44 | 0.5 | 33.13 | 2.38 | 62.56 | 63.38 | 34.75 | 3.4375 | 3.9375 | 5 | 6 | 445T | 69.88 | 93.88 | 4 | 6 | 0.5 | 0.81 | 52.5 | 73.75 | 2.5 | 80 | 0.175 | 0.175 | 40 | 105.88 | 56.88 | 52.44 | 69.69 | 50 | 55.12 | 50.06 | 10 | 1.25 | 0.63 | 32.63 | 2.88 | 66.63 | 34.75 | 4.9375 | 7
| 730H | 73 | 254T | 445T | 77.25 | 103.375 | 3.5 | 5 | 0.5 | 0.81 | 0.75 | 57 | 75.63 | 38.63 | 2.5 | 88 | 0.126 | 0.126 | 44 | 113.375 | 62.88 | 57.5 | 77.13 | 58.81 | 69.19 | 38.5 | 3.9375 | 9 | 1 | 0.5 | n/a | 54.31 | 37.13 | 2.38 | 6.87 | 81 | 56.94 | 67.1938 | 2 | 6 | 0.5 | 5.9062 | 5.5 | 6.0312 | 445T | 445T | 77.25 | 103.375 | 3.5 | 5 | 0.5 | 0.81 | 57 | 80.75 | 2.5 | 88 | 0.126 | 0.126 | 44 | 113.375 | 62.88 | 57.5 | 77.13 | 55.38 | 58.81 | 58.81 | 54.31 | 9 | 1 | 1 | 0.5 | 0.5 | 37.13 | 2.38 | 69.19 | 69.19 | 38.5 | 3.9375 | 3.9375 | 6 | 6 | 445T | 77.38 | 103.5 | 4 | 6 | 0.5 | 0.81 | 57 | 81.25 | 2.5 | 88 | 0.175 | 0.175 | 44 | 115.5 | 62.94 | 58 | 77.19 | 55.44 | 59.94 | 54.88 | 10 | 1.25 | 0.63 | 36.63 | 2.88 | 71.44 | 38.5 | 4.9375 | 7
Twin City BAE DWDI Fan Data (Up Discharge)
TYPE A | 122T | 12.2 | 143T | 254T | 13 | 17.5 | 1.5 | 1.5 | 0.188 | 0.44 | 0.375 | 11.5 | 7.75 | 0.875 | 1 | 19.75 | 0.07 | 0.07 | 9.875 | 20.5 | 9.31 | 12.94 | 9.25 | 12.38 | 16.25 | 6.44 | 1.4375 | 3 | 0.38 | 0.19 | n/a | 9.63 | 6.75 | 0.63 | 3.125 | 16.75 | 9.516 | 11.375 | 1.25 | 2.5 | 0.375 | 2.1562 | 2 | 2.2812 | 213T | 254T | 13 | 17.5 | 1.5 | 1.5 | 0.188 | 0.44 | 11.5 | n/a | 1 | 19.75 | 0.07 | 0.07 | 9.875 | 20.5 | 9.31 | 12.94 | 9.25 | n/a | 11.44 | 12.38 | 9.63 | 3 | 0.25 | 0.38 | 0.13 | 0.19 | 6.75 | 0.63 | 15.25 | 16.25 | 6.44 | 1.1875 | 1.4375 | 2.5 | 2.5 | 254T | 13.13 | 17.63 | 1.5 | 2 | 0.188 | 0.44 | 11.5 | n/a | 1.25 | 19.75 | 0.126 | 0.126 | 9.875 | 21.63 | 9.38 | 13 | 9.75 | n/a | 12.56 | 9.94 | 3.5 | 0.5 | 0.25 | 6.5 | 0.88 | 17.06 | 6.44 | 1.9375 | 3
| 135T | 13.5 | 143T | 254T | 14.31 | 19.5 | 1.5 | 1.5 | 0.188 | 0.44 | 0.375 | 12.75 | 8.75 | 1.25 | 1 | 21 | 0.07 | 0.07 | 10.5 | 22.5 | 10.25 | 14.25 | 10.25 | 13.38 | 17.25 | 7.13 | 1.6875 | 3 | 3.8 | 0.19 | n/a | 10.63 | 7.38 | 0.63 | 3.12 | 18 | 10.53 | 12.675 | 1.25 | 2.5 | 0.375 | 2.5312 | 2 | 2.6562 | 213T | 254T | 14.31 | 19.5 | 1.5 | 1.5 | 0.188 | 0.44 | 12.75 | n/a | 1 | 21 | 0.07 | 0.07 | 10.5 | 22.5 | 10.25 | 14.25 | 10.25 | n/a | 12.44 | 13.38 | 10.63 | 3 | 0.25 | 3.8 | 0.13 | 0.19 | 7.38 | 0.63 | 16.25 | 17.25 | 7.13 | 1.1875 | 1.6875 | 2.5 | 2.5 | 254T | 14.44 | 19.63 | 1.5 | 2 | 0.188 | 0.44 | 12.75 | n/a | 1.25 | 21 | 0.126 | 0.126 | 10.5 | 23.63 | 10.31 | 14.31 | 10.75 | n/a | 13.56 | 10.94 | 4 | 0.5 | 0.25 | 7.13 | 0.88 | 18.56 | 7.13 | 1.9375 | 3
| 150T | 15 | 143T | 256T | 15.88 | 21.5 | 1.5 | 1.5 | 0.188 | 0.44 | 0.375 | 14 | 9.94 | 1.565 | 1 | 22.75 | 0.07 | 0.07 | 11.375 | 24.5 | 11.38 | 15.81 | 11.44 | 14.38 | 18.75 | 7.88 | 1.6875 | 3.5 | 0.38 | 0.19 | n/a | 11.63 | 8.25 | 0.63 | 3.125 | 19.75 | 11.7 | 13.975 | 1.25 | 2.5 | 0.375 | 2.5312 | 2 | 2.6562 | 215T | 256T | 15.88 | 21.5 | 1.5 | 1.5 | 0.188 | 0.44 | 14 | n/a | 1 | 22.75 | 0.07 | 0.07 | 11.375 | 24.5 | 11.38 | 15.81 | 11.44 | n/a | 14.38 | 14.38 | 11.63 | 3.5 | 0.38 | 0.38 | 0.19 | 0.19 | 8.25 | 0.63 | 18.75 | 18.75 | 7.88 | 1.4375 | 1.6875 | 2.5 | 2.5 | 256T | 16 | 21.63 | 1.5 | 2 | 0.188 | 0.44 | 14 | n/a | 1.25 | 22.75 | 0.126 | 0.126 | 11.375 | 25.63 | 11.44 | 15.88 | 11.94 | n/a | 15.13 | 11.94 | 4 | 0.5 | 0.25 | 8 | 0.88 | 20.13 | 7.88 | 2.1875 | 3.5
| 165T | 16.5 | 143T | 256T | 17.44 | 23.625 | 1.5 | 2 | 0.188 | 0.44 | 0.375 | 15.25 | 11.13 | 2.005 | 1 | 24.25 | 0.07 | 0.07 | 12.125 | 27.625 | 12.5 | 17.38 | 12.63 | 15.56 | 20.06 | 8.69 | 1.9375 | 3.5 | 0.5 | 0.25 | n/a | 12.94 | 8.75 | 0.88 | 3.375 | 21.25 | 12.87 | 15.3563 | 1.25 | 3 | 0.375 | 2.9062 | 2.5 | 3.0312 | 215T | 256T | 17.44 | 23.625 | 1.5 | 2 | 0.188 | 0.44 | 15.25 | n/a | 1 | 24.25 | 0.07 | 0.07 | 12.125 | 27.625 | 12.5 | 17.38 | 12.63 | n/a | 15.44 | 15.56 | 12.94 | 3.5 | 0.38 | 0.5 | 0.19 | 0.25 | 8.75 | 0.88 | 19.81 | 20.06 | 8.69 | 1.4375 | 1.9375 | 2.5 | 3 | 256T | 17.56 | 23.75 | 1.5 | 2 | 0.188 | 0.44 | 15.25 | n/a | 1.25 | 24.25 | 0.126 | 0.126 | 12.125 | 27.75 | 12.56 | 17.44 | 13.13 | n/a | 16.19 | 13 | 4.5 | 0.5 | 0.25 | 8.75 | 0.88 | 21.69 | 8.69 | 2.1875 | 3.5
| 182T | 18.2 | 145T | 284T | 19.38 | 26 | 1.5 | 2 | 0.188 | 0.44 | 0.375 | 16.75 | 12.5 | 2.5 | 1.25 | 26 | 0.097 | 0.07 | 13 | 30 | 13.81 | 19.31 | 14 | 16.75 | 21.75 | 9.63 | 1.9375 | 4 | 0.5 | 0.25 | n/a | 14.13 | 9.63 | 0.88 | 3.37 | 23 | 14.196 | 16.9 | 1.25 | 3 | 0.375 | 2.9062 | 2.5 | 3.0312 | 254T | 284T | 19.38 | 26 | 1.5 | 2 | 0.188 | 0.44 | 16.75 | n/a | 1.25 | 26 | 0.097 | 0.07 | 13 | 30 | 13.81 | 19.31 | 14 | n/a | 16.63 | 16.75 | 14.13 | 4 | 0.38 | 0.5 | 0.19 | 0.25 | 9.63 | 0.88 | 21.5 | 21.75 | 9.63 | 1.6875 | 1.9375 | 2.5 | 3 | 284T | 19.5 | 26.13 | 2 | 2 | 0.25 | 0.56 | 16.75 | n/a | 1.25 | 27 | 0.126 | 0.126 | 13.5 | 30.13 | 13.88 | 19.38 | 14.5 | n/a | 17.38 | 14.19 | 4.5 | 0.5 | 0.25 | 9.63 | 0.88 | 22.88 | 9.63 | 2.1875 | 3.5
| 200T | 20 | 145T | 286T | 21.19 | 28.5 | 1.5 | 2 | 0.188 | 0.56 | 0.5 | 18.25 | 13.81 | 2.81 | 1.25 | 28 | 0.097 | 0.07 | 14 | 32.5 | 15.19 | 21.13 | 15.31 | 18.56 | 23.56 | 10.56 | 2.1875 | 4 | 0.5 | 0.25 | n/a | 15.38 | 10.63 | 0.88 | 3.37 | 25 | 15.6 | 18.525 | 1.25 | 3.5 | 0.375 | 3.2812 | 3 | 3.4062 | 254T | 286T | 21.19 | 28.5 | 1.5 | 2 | 0.188 | 0.56 | 18.25 | n/a | 1.25 | 28 | 0.097 | 0.07 | 14 | 32.5 | 15.19 | 21.13 | 15.31 | n/a | 17.88 | 18.56 | 15.38 | 4 | 0.38 | 0.5 | 0.19 | 0.25 | 10.63 | 0.88 | 22.75 | 23.56 | 10.56 | 1.6875 | 2.1875 | 2.5 | 3.5 | 286T | 21.31 | 28.63 | 2 | 2 | 0.25 | 0.56 | 18.25 | n/a | 1.25 | 29 | 0.126 | 0.126 | 14.5 | 32.63 | 15.25 | 21.19 | 15.81 | n/a | 19.13 | 15.44 | 5 | 0.63 | 0.31 | 10.63 | 0.88 | 25.25 | 10.56 | 2.4375 | 3.5
| 222T | 22.2 | 145T | 324T | 23.56 | 31.625 | 2 | 2 | 0.25 | 0.56 | 0.5 | 20.5 | 15.69 | 4.065 | 1.25 | 31.25 | 0.097 | 0.07 | 15.625 | 35.625 | 16.81 | 23.5 | 17.19 | 20.63 | 26.25 | 11.75 | 2.4375 | 4.5 | 0.63 | 0.31 | n/a | 16.94 | 11.75 | 0.88 | 3.875 | 27.25 | 17.316 | 20.5563 | 1.25 | 3.5 | 0.375 | 3.6562 | 3 | 3.7812 | 256T | 324T | 23.56 | 31.625 | 2 | 2 | 0.25 | 0.56 | 20.5 | n/a | 1.25 | 31.25 | 0.097 | 0.07 | 15.625 | 35.625 | 16.81 | 23.5 | 17.19 | n/a | 19.56 | 20.63 | 16.94 | 4.5 | 0.5 | 0.63 | 0.25 | 0.31 | 11.75 | 0.88 | 25.06 | 26.25 | 11.75 | 1.9375 | 2.4375 | 3 | 3.5 | 324T | 23.69 | 31.75 | 2.5 | 2.5 | 0.25 | 0.56 | 20.5 | n/a | 1.25 | 32.25 | 0.126 | 0.126 | 16.125 | 36.75 | 16.88 | 23.56 | 17.69 | n/a | 20.69 | 17.25 | 5 | 0.63 | 0.31 | 11.5 | 1.13 | 26.81 | 11.75 | 2.4375 | 3.5
TYPE B | 245T | 24.5 | 143T | 326T | 25.94 | 34.875 | 2 | 2 | 0.25 | 0.56 | 0.5 | 22.5 | 17.5 | 4.75 | 1.25 | 33.5 | 0.097 | 0.07 | 16.75 | 38.875 | 18.5 | 25.88 | 19 | 22.31 | 28.44 | 12.94 | 2.4375 | 5 | 0.63 | 0.31 | n/a | 18.56 | 12.88 | 0.88 | 3.87 | 29.5 | 19.11 | 22.6687 | 1.5 | 3.5 | 0.375 | 3.6562 | 3 | 3.7812 | 284T | 326T | 25.94 | 34.875 | 2 | 2 | 0.25 | 0.56 | 22.5 | n/a | 1.25 | 33.5 | 0.097 | 0.07 | 16.75 | 38.875 | 18.5 | 25.88 | 19 | n/a | 21.81 | 22.31 | 18.56 | 5 | 0.5 | 0.63 | 0.25 | 0.31 | 12.88 | 0.88 | 27.81 | 28.44 | 12.94 | 2.1875 | 2.4375 | 3.5 | 3.5 | 326T | 26.19 | 35 | 2.5 | 2.5 | 0.25 | 0.56 | 22.5 | n/a | 1.5 | 34.5 | 0.175 | 0.175 | 17.25 | 40 | 18.63 | 26 | 19.5 | n/a | 22.38 | 18.88 | 6 | 0.63 | 0.31 | 12.63 | 1.13 | 29.5 | 12.94 | 2.4375 | 3.5
| 270T | 27 | 145T | 326T | 28.63 | 38.25 | 2 | 2 | 0.25 | 0.56 | 0.5 | 24.75 | 19.44 | 5.44 | 1.5 | 36 | 0.097 | 0.07 | 18 | 42.25 | 20.44 | 28.56 | 20.94 | 24.31 | 30.44 | 14.25 | 2.6875 | 5 | 0.63 | 0.31 | n/a | 20.25 | 14.13 | 0.88 | 3.87 | 32 | 21.06 | 24.8625 | 1.5 | 4 | 0.5 | 4.0312 | 3.5 | 4.1562 | 284T | 326T | 28.63 | 38.25 | 2 | 2 | 0.25 | 0.56 | 24.75 | n/a | 1.5 | 36 | 0.097 | 0.07 | 18 | 42.25 | 20.44 | 28.56 | 20.94 | n/a | 23.5 | 24.31 | 20.25 | 5 | 0.5 | 0.63 | 0.25 | 0.31 | 14.13 | 0.88 | 29.5 | 30.44 | 14.25 | 2.1875 | 2.6875 | 3.5 | 4 | 326T | 28.88 | 38.5 | 2.5 | 2.5 | 0.25 | 0.56 | 24.75 | n/a | 1.5 | 37 | 0.175 | 0.175 | 18.5 | 43.5 | 20.56 | 28.69 | 21.44 | n/a | 24.44 | 20.63 | 6 | 0.63 | 0.31 | 13.88 | 1.13 | 31.56 | 14.25 | 2.6875 | 4
| 300T | 30 | 143T | 364T | 31.81 | 42.75 | 2.5 | 2.5 | 0.25 | 0.56 | 0.5 | 28.5 | 21.81 | 6.31 | 1.5 | 41 | 0.126 | 0.097 | 20.5 | 47.75 | 22.75 | 31.75 | 23.31 | 26.25 | 32.88 | 15.81 | 2.4375 | 5.5 | 0.63 | 0.31 | n/a | 22.75 | 15.88 | 1.13 | 4.62 | 36 | 23.4 | 27.7875 | 1.5 | 3.5 | 0.375 | 3.6562 | 3 | 3.7812 | 286T | 364T | 31.81 | 42.75 | 2.5 | 2.5 | 0.25 | 0.56 | 28.5 | n/a | 1.5 | 41 | 0.126 | 0.097 | 20.5 | 47.75 | 22.75 | 31.75 | 23.31 | n/a | 26.25 | 26.25 | 22.75 | 5.5 | 0.63 | 0.63 | 0.31 | 0.31 | 15.88 | 1.13 | 32.88 | 32.88 | 15.81 | 2.4375 | 2.4375 | 3.5 | 3.5 | 364T | 32 | 42.88 | 3 | 3 | 0.313 | 0.81 | 27.5 | n/a | 1.5 | 42 | 0.175 | 0.175 | 21 | 48.88 | 22.81 | 31.81 | 23.81 | n/a | 26.63 | 23.06 | 7 | 0.63 | 0.31 | 15.63 | 1.38 | 34.75 | 15.81 | 2.6875 | 4
| 330T | 33 | 143T | 365T | 35.13 | 46.75 | 2.5 | 2.5 | 0.25 | 0.56 | 0.5 | 31 | 24.25 | 7.25 | 1.5 | 44 | 0.126 | 0.097 | 22 | 51.75 | 25 | 35.06 | 25.75 | 28.25 | 34.88 | 17.5 | 2.4375 | 5.5 | 0.63 | 0.31 | n/a | 24.75 | 17.38 | 1.13 | 4.62 | 39 | 25.74 | 30.3875 | 1.5 | 4 | 0.5 | 3.6562 | 3.5 | 3.7812 | 324T | 365T | 35.13 | 46.75 | 2.5 | 2.5 | 0.25 | 0.56 | 31 | n/a | 1.5 | 44 | 0.126 | 0.097 | 22 | 51.75 | 25 | 35.06 | 25.75 | n/a | 28.25 | 28.25 | 24.75 | 5.5 | 0.63 | 0.63 | 0.31 | 0.31 | 17.38 | 1.13 | 34.88 | 34.88 | 17.5 | 2.4375 | 2.4375 | 3.5 | 4 | 365T | 35.31 | 46.88 | 3 | 3 | 0.313 | 0.81 | 30 | n/a | 1.5 | 45 | 0.175 | 0.175 | 22.5 | 52.88 | 25.06 | 35.13 | 26.25 | n/a | 28.44 | 25.06 | 7 | 0.75 | 0.38 | 17.13 | 1.38 | 36.69 | 17.5 | 2.9375 | 4
| 365T | 36.5 | 143T | 404T | 38.69 | 51.875 | 2.5 | 2.5 | 0.25 | 0.56 | 0.5 | 33.5 | 27 | 8 | 1.5 | 48 | 0.126 | 0.097 | 24 | 56.875 | 27.75 | 38.63 | 28.5 | 31.13 | 37.75 | 19.25 | 2.6875 | 5.5 | 0.63 | 0.31 | n/a | 27.31 | 18.88 | 1.13 | 5.12 | 43 | 28.47 | 33.7188 | 1.5 | 4 | 0.5 | 4.0312 | 3.5 | 4.1562 | 324T | 404T | 38.69 | 51.875 | 2.5 | 2.5 | 0.25 | 0.56 | 33.5 | n/a | 1.5 | 48 | 0.126 | 0.097 | 24 | 56.875 | 27.75 | 38.63 | 28.5 | n/a | 31.13 | 31.13 | 27.31 | 5.5 | 0.63 | 0.63 | 0.31 | 0.31 | 18.88 | 1.13 | 37.75 | 37.75 | 19.25 | 2.6875 | 2.6875 | 4 | 4 | 404T | 38.88 | 52 | 3 | 3 | 0.313 | 0.81 | 33.5 | n/a | 1.5 | 49 | 0.175 | 0.175 | 24.5 | 58 | 27.81 | 38.69 | 29 | n/a | 31 | 27.63 | 7 | 0.75 | 0.38 | 18.63 | 1.38 | 39.25 | 19.25 | 2.9375 | 5
TYPE C | 402T | 40.2 | 145T | 404T | 42.63 | 57.25 | 3 | 3 | 0.313 | 0.81 | 0.75 | 37 | 30 | 9.75 | 1.5 | 52.5 | 0.126 | 0.097 | 26.25 | 63.25 | 30.56 | 42.56 | 31.5 | 33.81 | 40.94 | 21.25 | 2.6875 | 6 | 0.63 | 0.31 | n/a | 30.25 | 20.88 | 1.38 | 5.37 | 46.5 | 31.356 | 37.2125 | 1.75 | 4 | 0.5 | 4.0312 | 3.5 | 4.1562 | 326T | 404T | 42.63 | 57.25 | 3 | 3 | 0.313 | 0.81 | 37 | n/a | 1.5 | 52.5 | 0.126 | 0.097 | 26.25 | 63.25 | 30.56 | 42.56 | 31.5 | n/a | 33.5 | 33.81 | 30.25 | 6 | 0.63 | 0.63 | 0.31 | 0.31 | 20.88 | 1.38 | 40.63 | 40.94 | 21.25 | 2.4375 | 2.6875 | 4 | 4 | 404T | 42.81 | 57.38 | 3 | 4 | 0.313 | 0.81 | 37 | n/a | 2 | 52.5 | 0.175 | 0.175 | 26.25 | 65.38 | 30.63 | 42.63 | 32 | n/a | 35.06 | 30.81 | 8 | 0.88 | 0.44 | 20.38 | 1.88 | 44.38 | 21.25 | 3.4375 | 5
| 445T | 44.5 | 182T | 405T | 47.13 | 63.125 | 3 | 3 | 0.313 | 0.81 | 0.75 | 40 | 33.38 | 11.13 | 1.5 | 56.5 | 0.126 | 0.097 | 28.25 | 69.125 | 33.75 | 47.06 | 34.88 | 36.56 | 43.81 | 23.5 | 2.9375 | 6 | 0.75 | 0.38 | n/a | 33.19 | 22.88 | 1.38 | 5.37 | 50.5 | 34.71 | 41.0312 | 1.75 | 5 | 0.5 | 4.4062 | 4.5 | 4.5312 | 364T | 405T | 47.13 | 63.125 | 3 | 3 | 0.313 | 0.81 | 40 | n/a | 1.5 | 56.5 | 0.126 | 0.097 | 28.25 | 69.125 | 33.75 | 47.06 | 34.88 | n/a | 36.44 | 36.56 | 33.19 | 6 | 0.63 | 0.75 | 0.31 | 0.38 | 22.88 | 1.38 | 43.56 | 43.81 | 23.5 | 2.4375 | 2.9375 | 4 | 5 | 405T | 47.31 | 63.25 | 3 | 4 | 0.313 | 0.81 | 40 | n/a | 2 | 56.5 | 0.175 | 0.175 | 28.25 | 71.25 | 33.81 | 47.13 | 35.38 | n/a | 38 | 33.75 | 8 | 0.88 | 0.44 | 22.38 | 1.88 | 47.31 | 23.5 | 3.4375 | 5
| 490T | 49 | 182T | 445T | 51.94 | 69.5 | 3 | 3 | 0.313 | 0.81 | 0.75 | 44 | 37 | 12.25 | 2 | 61.5 | 0.126 | 0.097 | 30.75 | 75.5 | 37.19 | 51.88 | 38.5 | 41.13 | 49.44 | 25.88 | 3.4375 | 7 | 0.88 | 0.44 | n/a | 36.38 | 25.38 | 1.38 | 5.37 | 55.5 | 38.22 | 45.175 | 1.75 | 5 | 0.5 | 5.1562 | 4.5 | 5.2812 | 365T | 445T | 51.94 | 69.5 | 3 | 3 | 0.313 | 0.81 | 44 | n/a | 2 | 61.5 | 0.126 | 0.097 | 30.75 | 75.5 | 37.19 | 51.88 | 38.5 | n/a | 39.94 | 41.13 | 36.38 | 7 | 0.63 | 0.88 | 0.31 | 0.44 | 25.38 | 1.38 | 48.06 | 49.44 | 25.88 | 2.6875 | 3.4375 | 4 | 5 | 445T | 52.13 | 69.63 | 3 | 4 | 0.313 | 0.81 | 44 | n/a | 2 | 61.5 | 0.175 | 0.175 | 30.75 | 77.63 | 37.25 | 51.94 | 39 | n/a | 41.94 | 36.94 | 9 | 1 | 0.5 | 24.88 | 1.88 | 52.31 | 25.88 | 3.9375 | 6
| 542T | 54.2 | 254T | 445T | 57.38 | 77 | 3 | 4 | 0.313 | 0.81 | 0.75 | 49 | 41.06 | 13.56 | 2 | 67 | 0.126 | 0.097 | 33.5 | 85 | 41.19 | 57.31 | 42.56 | 44.19 | 51.5 | 28.63 | 3.4375 | 6 | 0.88 | 0.44 | n/a | 40.63 | 27.63 | 1.88 | 5.87 | 61 | 42.276 | 50.05 | 1.75 | 5 | 0.5 | 5.1562 | 4.5 | 5.2812 | 404T | 445T | 57.38 | 77 | 3 | 4 | 0.313 | 0.81 | 49 | n/a | 2 | 67 | 0.126 | 0.097 | 33.5 | 85 | 41.19 | 57.31 | 42.56 | n/a | 43.75 | 44.19 | 40.63 | 6 | 0.75 | 0.88 | 0.38 | 0.44 | 27.63 | 1.88 | 51 | 51.5 | 28.63 | 2.9375 | 3.4375 | 4 | 5 | 445T | 57.56 | 77.13 | 3.5 | 5 | 0.5 | 0.81 | 49 | n/a | 2.5 | 67 | 0.175 | 0.175 | 33.5 | 87.13 | 41.25 | 57.38 | 43.06 | n/a | 45.69 | 41.19 | 9 | 1 | 0.5 | 27.13 | 2.38 | 56.06 | 28.63 | 3.9375 | 6
| 600T | 60 | 254T | 445T | 63.5 | 85 | 3 | 4 | 0.313 | 0.81 | 0.75 | 54 | 45.69 | 15.19 | 2 | 73 | 0.126 | 0.097 | 36.5 | 93 | 45.56 | 63.44 | 47.19 | 49.63 | 59 | 31.69 | 3.9375 | 8 | 1 | 0.5 | n/a | 44.63 | 30.63 | 1.88 | 5.87 | 67 | 46.8 | 55.25 | 2 | 6 | 0.5 | 5.9062 | 5.5 | 6.0312 | 405T | 445T | 63.5 | 85 | 3 | 4 | 0.313 | 0.81 | 54 | n/a | 2 | 73 | 0.126 | 0.097 | 36.5 | 93 | 45.56 | 63.44 | 47.19 | n/a | 48.88 | 49.63 | 44.63 | 8 | 0.88 | 1 | 0.44 | 0.5 | 30.63 | 1.88 | 58.19 | 59 | 31.69 | 3.4375 | 3.9375 | 5 | 6 | 445T | 63.69 | 85.13 | 3.5 | 5 | 0.5 | 0.81 | 54 | n/a | 2.5 | 74 | 0.175 | 0.175 | 37 | 95.13 | 45.63 | 63.5 | 47.69 | n/a | 50.44 | 45.19 | 9.5 | 1 | 0.5 | 30.13 | 2.38 | 61.31 | 31.69 | 4.4375 | 7
| 660T | 66 | 254T | 445T | 69.69 | 93.75 | 3.5 | 5 | 0.5 | 0.81 | 0.75 | 59 | 50.44 | 17.44 | 2.5 | 80 | 0.126 | 0.097 | 40 | 103.75 | 49.94 | 69.63 | 51.94 | 54.06 | 63.38 | 34.75 | 3.9375 | 8 | 1 | 0.5 | n/a | 49.5 | 33.13 | 2.38 | 6.87 | 73 | 51.48 | 60.9375 | 2 | 6 | 0.5 | 5.9062 | 5.5 | 6.0312 | 405T | 445T | 69.69 | 93.75 | 3.5 | 5 | 0.5 | 0.81 | 59 | n/a | 2.5 | 80 | 0.126 | 0.097 | 40 | 103.75 | 49.94 | 69.63 | 51.94 | n/a | 53.25 | 54.06 | 49.5 | 8 | 0.88 | 1 | 0.44 | 0.5 | 33.13 | 2.38 | 62.56 | 63.38 | 34.75 | 3.4375 | 3.9375 | 5 | 6 | 445T | 69.88 | 93.88 | 4 | 6 | 0.5 | 0.81 | 59 | n/a | 2.5 | 80 | 0.175 | 0.175 | 40 | 105.88 | 50 | 69.69 | 52.44 | n/a | 55.12 | 50.06 | 10 | 1.25 | 0.63 | 32.63 | 2.88 | 66.63 | 34.75 | 4.9375 | 7
| 730T | 73 | 254T | 445T | 77.25 | 103.375 | 3.5 | 5 | 0.5 | 0.81 | 0.75 | 64.5 | 56 | 19 | 2.5 | 88 | 0.126 | 0.126 | 44 | 113.375 | 55.38 | 77.13 | 57.5 | 58.81 | 69.19 | 38.5 | 3.9375 | 9 | 1 | 0.5 | n/a | 54.31 | 37.13 | 2.38 | 6.87 | 81 | 56.94 | 67.1938 | 2 | 6 | 0.5 | 5.9062 | 5.5 | 6.0312 | 445T | 445T | 77.25 | 103.375 | 3.5 | 5 | 0.5 | 0.81 | 64.5 | n/a | 2.5 | 88 | 0.126 | 0.126 | 44 | 113.375 | 55.38 | 77.13 | 57.5 | n/a | 58.81 | 58.81 | 54.31 | 9 | 1 | 1 | 0.5 | 0.5 | 37.13 | 2.38 | 69.19 | 69.19 | 38.5 | 3.9375 | 3.9375 | 6 | 6 | 445T | 77.38 | 103.5 | 4 | 6 | 0.5 | 0.81 | 64.5 | n/a | 2.5 | 88 | 0.175 | 0.175 | 44 | 115.5 | 55.44 | 77.19 | 58 | n/a | 59.94 | 54.88 | 10 | 1.25 | 0.63 | 36.63 | 2.88 | 71.44 | 38.5 | 4.9375 | 7
Twin City BAE DWDI Fan Data (Down Discharge)
TYPE A | 122B | 12.2 | 143T | 254T | 13 | 17.5 | 1.5 | 1.5 | 0.188 | 0.44 | 0.375 | 9.75 | 9.06 | 2.185 | 1 | 19.75 | 0.07 | 0.07 | 9.875 | 20.5 | 9.31 | 13.44 | 10.56 | 12.38 | 16.25 | 6.44 | 1.4375 | 3 | 0.38 | 0.19 | n/a | 9.63 | 6.75 | 0.63 | 3.125 | 16.75 | 9.516 | 11.375 | 1.25 | 2.5 | 0.375 | 2.1562 | 2 | 2.2812 | 213T | 254T | 13 | 17.5 | 1.5 | 1.5 | 0.188 | 0.44 | n/a | 9.75 | 1 | 19.75 | 0.07 | 0.07 | 9.875 | 20.5 | 9.31 | 13.44 | n/a | 10.56 | 11.44 | 12.38 | 9.63 | 3 | 0.25 | 0.38 | 0.13 | 0.19 | 6.75 | 0.63 | 15.25 | 16.25 | 6.44 | 1.1875 | 1.4375 | 2.5 | 2.5 | 254T | 13.13 | 17.63 | 1.5 | 2 | 0.188 | 0.44 | n/a | 9.75 | 1.25 | 19.75 | 0.126 | 0.126 | 9.875 | 21.63 | 9.38 | 13.75 | n/a | 10.63 | 12.56 | 9.94 | 3.5 | 0.5 | 0.25 | 6.5 | 0.88 | 17.06 | 6.44 | 1.9375 | 3
| 135B | 13.5 | 143T | 254T | 14.31 | 19.5 | 1.5 | 1.5 | 0.188 | 0.44 | 0.375 | 10.75 | 10.13 | 2.63 | 1 | 21 | 0.07 | 0.07 | 10.5 | 22.5 | 10.25 | 14.75 | 11.63 | 13.38 | 17.25 | 7.13 | 1.6875 | 3 | 3.8 | 0.19 | n/a | 10.63 | 7.38 | 0.63 | 3.12 | 18 | 10.53 | 12.675 | 1.25 | 2.5 | 0.375 | 2.5312 | 2 | 2.6562 | 213T | 254T | 14.31 | 19.5 | 1.5 | 1.5 | 0.188 | 0.44 | n/a | 10.75 | 1 | 21 | 0.07 | 0.07 | 10.5 | 22.5 | 10.25 | 14.75 | n/a | 11.63 | 12.44 | 13.38 | 10.63 | 3 | 0.25 | 3.8 | 0.13 | 0.19 | 7.38 | 0.63 | 16.25 | 17.25 | 7.13 | 1.1875 | 1.6875 | 2.5 | 2.5 | 254T | 14.44 | 19.63 | 1.5 | 2 | 0.188 | 0.44 | n/a | 10.75 | 1.25 | 21 | 0.126 | 0.126 | 10.5 | 23.63 | 10.31 | 15.06 | n/a | 11.69 | 13.56 | 10.94 | 4 | 0.5 | 0.25 | 7.13 | 0.88 | 18.56 | 7.13 | 1.9375 | 3
| 150B | 15 | 143T | 256T | 15.88 | 21.5 | 1.5 | 1.5 | 0.188 | 0.44 | 0.375 | 11.94 | 11.38 | 3.005 | 1 | 22.75 | 0.07 | 0.07 | 11.375 | 24.5 | 11.38 | 16.31 | 12.88 | 14.38 | 18.75 | 7.88 | 1.6875 | 3.5 | 0.38 | 0.19 | n/a | 11.63 | 8.25 | 0.63 | 3.125 | 19.75 | 11.7 | 13.975 | 1.25 | 2.5 | 0.375 | 2.5312 | 2 | 2.6562 | 215T | 256T | 15.88 | 21.5 | 1.5 | 1.5 | 0.188 | 0.44 | n/a | 11.94 | 1 | 22.75 | 0.07 | 0.07 | 11.375 | 24.5 | 11.38 | 16.31 | n/a | 12.88 | 14.38 | 14.38 | 11.63 | 3.5 | 0.38 | 0.38 | 0.19 | 0.19 | 8.25 | 0.63 | 18.75 | 18.75 | 7.88 | 1.4375 | 1.6875 | 2.5 | 2.5 | 256T | 16 | 21.63 | 1.5 | 2 | 0.188 | 0.44 | n/a | 11.94 | 1.25 | 22.75 | 0.126 | 0.126 | 11.375 | 25.63 | 11.44 | 16.63 | n/a | 12.94 | 15.13 | 11.94 | 4 | 0.5 | 0.25 | 8 | 0.88 | 20.13 | 7.88 | 2.1875 | 3.5
| 165B | 16.5 | 143T | 256T | 17.44 | 23.625 | 1.5 | 2 | 0.188 | 0.44 | 0.375 | 13.13 | 12.63 | 3.505 | 1 | 24.25 | 0.07 | 0.07 | 12.125 | 27.625 | 12.5 | 18.38 | 14.13 | 15.56 | 20.06 | 8.69 | 1.9375 | 3.5 | 0.5 | 0.25 | n/a | 12.94 | 8.75 | 0.88 | 3.375 | 21.25 | 12.87 | 15.3563 | 1.25 | 3 | 0.375 | 2.9062 | 2.5 | 3.0312 | 215T | 256T | 17.44 | 23.625 | 1.5 | 2 | 0.188 | 0.44 | n/a | 13.13 | 1 | 24.25 | 0.07 | 0.07 | 12.125 | 27.625 | 12.5 | 18.38 | n/a | 14.13 | 15.44 | 15.56 | 12.94 | 3.5 | 0.38 | 0.5 | 0.19 | 0.25 | 8.75 | 0.88 | 19.81 | 20.06 | 8.69 | 1.4375 | 1.9375 | 2.5 | 3 | 256T | 17.56 | 23.75 | 1.5 | 2 | 0.188 | 0.44 | n/a | 13.13 | 1.25 | 24.25 | 0.126 | 0.126 | 12.125 | 27.75 | 12.56 | 18.19 | n/a | 14.19 | 16.19 | 13 | 4.5 | 0.5 | 0.25 | 8.75 | 0.88 | 21.69 | 8.69 | 2.1875 | 3.5
| 182B | 18.2 | 145T | 284T | 19.38 | 26 | 1.5 | 2 | 0.188 | 0.44 | 0.375 | 14.5 | 14.19 | 4.19 | 1.25 | 26 | 0.097 | 0.07 | 13 | 30 | 13.81 | 20.06 | 15.69 | 16.75 | 21.75 | 9.63 | 1.9375 | 4 | 0.5 | 0.25 | n/a | 14.13 | 9.63 | 0.88 | 3.37 | 23 | 14.196 | 16.9 | 1.25 | 3 | 0.375 | 2.9062 | 2.5 | 3.0312 | 254T | 284T | 19.38 | 26 | 1.5 | 2 | 0.188 | 0.44 | n/a | 14.5 | 1.25 | 26 | 0.097 | 0.07 | 13 | 30 | 13.81 | 20.06 | n/a | 15.69 | 16.63 | 16.75 | 14.13 | 4 | 0.38 | 0.5 | 0.19 | 0.25 | 9.63 | 0.88 | 21.5 | 21.75 | 9.63 | 1.6875 | 1.9375 | 2.5 | 3 | 284T | 19.5 | 26.13 | 2 | 2 | 0.25 | 0.56 | n/a | 14.5 | 1.25 | 27 | 0.126 | 0.126 | 13.5 | 30.13 | 13.88 | 20.13 | n/a | 15.75 | 17.38 | 14.19 | 4.5 | 0.5 | 0.25 | 9.63 | 0.88 | 22.88 | 9.63 | 2.1875 | 3.5
| 200B | 20 | 145T | 286T | 21.19 | 28.5 | 1.5 | 2 | 0.188 | 0.56 | 0.5 | 15.81 | 15.81 | 4.81 | 1.25 | 28 | 0.097 | 0.07 | 14 | 32.5 | 15.19 | 21.88 | 17.31 | 18.56 | 23.56 | 10.56 | 2.1875 | 4 | 0.5 | 0.25 | n/a | 15.38 | 10.63 | 0.88 | 3.37 | 25 | 15.6 | 18.525 | 1.25 | 3.5 | 0.375 | 3.2812 | 3 | 3.4062 | 254T | 286T | 21.19 | 28.5 | 1.5 | 2 | 0.188 | 0.56 | n/a | 15.81 | 1.25 | 28 | 0.097 | 0.07 | 14 | 32.5 | 15.19 | 21.88 | n/a | 17.31 | 17.88 | 18.56 | 15.38 | 4 | 0.38 | 0.5 | 0.19 | 0.25 | 10.63 | 0.88 | 22.75 | 23.56 | 10.56 | 1.6875 | 2.1875 | 2.5 | 3.5 | 286T | 21.31 | 28.63 | 2 | 2 | 0.25 | 0.56 | n/a | 15.81 | 1.25 | 29 | 0.126 | 0.126 | 14.5 | 32.63 | 15.25 | 21.94 | n/a | 17.38 | 19.13 | 15.44 | 5 | 0.63 | 0.31 | 10.63 | 0.88 | 25.25 | 10.56 | 2.4375 | 3.5
| 222B | 22.2 | 145T | 324T | 23.56 | 31.625 | 2 | 2 | 0.25 | 0.56 | 0.5 | 17.69 | 17.56 | 5.935 | 1.25 | 31.25 | 0.097 | 0.07 | 15.625 | 35.625 | 16.81 | 24.25 | 19.06 | 20.63 | 26.25 | 11.75 | 2.4375 | 4.5 | 0.63 | 0.31 | n/a | 16.94 | 11.75 | 0.88 | 3.875 | 27.25 | 17.316 | 20.5563 | 1.25 | 3.5 | 0.375 | 3.6562 | 3 | 3.7812 | 256T | 324T | 23.56 | 31.625 | 2 | 2 | 0.25 | 0.56 | n/a | 17.69 | 1.25 | 31.25 | 0.097 | 0.07 | 15.625 | 35.625 | 16.81 | 24.25 | n/a | 19.06 | 19.56 | 20.63 | 16.94 | 4.5 | 0.5 | 0.63 | 0.25 | 0.31 | 11.75 | 0.88 | 25.06 | 26.25 | 11.75 | 1.9375 | 2.4375 | 3 | 3.5 | 324T | 23.69 | 31.75 | 2.5 | 2.5 | 0.25 | 0.56 | n/a | 17.69 | 1.25 | 32.25 | 0.126 | 0.126 | 16.125 | 36.75 | 16.88 | 24.81 | n/a | 19.13 | 20.69 | 17.25 | 5 | 0.63 | 0.31 | 11.5 | 1.13 | 26.81 | 11.75 | 2.4375 | 3.5
TYPE B | 245B | 24.5 | 143T | 326T | 25.94 | 34.875 | 2 | 2 | 0.25 | 0.56 | 0.5 | 19.5 | 19.5 | 6.75 | 1.25 | 33.5 | 0.097 | 0.07 | 16.75 | 38.875 | 18.5 | 26.63 | 21 | 22.31 | 28.44 | 12.94 | 2.4375 | 5 | 0.63 | 0.31 | n/a | 18.56 | 12.88 | 0.88 | 3.87 | 29.5 | 19.11 | 22.6687 | 1.5 | 3.5 | 0.375 | 3.6562 | 3 | 3.7812 | 284T | 326T | 25.94 | 34.875 | 2 | 2 | 0.25 | 0.56 | n/a | 19.5 | 1.25 | 33.5 | 0.097 | 0.07 | 16.75 | 38.875 | 18.5 | 26.63 | n/a | 21 | 21.81 | 22.31 | 18.56 | 5 | 0.5 | 0.63 | 0.25 | 0.31 | 12.88 | 0.88 | 27.81 | 28.44 | 12.94 | 2.1875 | 2.4375 | 3.5 | 3.5 | 326T | 26.19 | 35 | 2.5 | 2.5 | 0.25 | 0.56 | n/a | 19.5 | 1.5 | 34.5 | 0.175 | 0.175 | 17.25 | 40 | 18.63 | 27 | n/a | 21.13 | 22.38 | 18.88 | 6 | 0.63 | 0.31 | 12.63 | 1.13 | 29.5 | 12.94 | 2.4375 | 3.5
| 270B | 27 | 145T | 326T | 28.63 | 38.25 | 2 | 2 | 0.25 | 0.56 | 0.5 | 21.44 | 21.69 | 7.69 | 1.5 | 36 | 0.097 | 0.07 | 18 | 42.25 | 20.44 | 29.06 | 23.19 | 24.31 | 30.44 | 14.25 | 2.6875 | 5 | 0.63 | 0.31 | n/a | 20.25 | 14.13 | 0.88 | 3.87 | 32 | 21.06 | 24.8625 | 1.5 | 4 | 0.5 | 4.0312 | 3.5 | 4.1562 | 284T | 326T | 28.63 | 38.25 | 2 | 2 | 0.25 | 0.56 | n/a | 21.44 | 1.5 | 36 | 0.097 | 0.07 | 18 | 42.25 | 20.44 | 29.06 | n/a | 23.19 | 23.5 | 24.31 | 20.25 | 5 | 0.5 | 0.63 | 0.25 | 0.31 | 14.13 | 0.88 | 29.5 | 30.44 | 14.25 | 2.1875 | 2.6875 | 3.5 | 4 | 326T | 28.88 | 38.5 | 2.5 | 2.5 | 0.25 | 0.56 | n/a | 21.44 | 1.5 | 37 | 0.175 | 0.175 | 18.5 | 43.5 | 20.56 | 29.69 | n/a | 23.31 | 24.44 | 20.63 | 6 | 0.63 | 0.31 | 13.88 | 1.13 | 31.56 | 14.25 | 2.6875 | 4
| 300B | 30 | 143T | 364T | 31.81 | 42.75 | 2.5 | 2.5 | 0.25 | 0.56 | 0.5 | 23.81 | 24.25 | 8.75 | 1.5 | 41 | 0.126 | 0.097 | 20.5 | 47.75 | 22.75 | 32.75 | 25.75 | 26.25 | 32.88 | 15.81 | 2.4375 | 5.5 | 0.63 | 0.31 | n/a | 22.75 | 15.88 | 1.13 | 4.62 | 36 | 23.4 | 27.7875 | 1.5 | 3.5 | 0.375 | 3.6562 | 3 | 3.7812 | 286T | 364T | 31.81 | 42.75 | 2.5 | 2.5 | 0.25 | 0.56 | n/a | 23.81 | 1.5 | 41 | 0.126 | 0.097 | 20.5 | 47.75 | 22.75 | 32.75 | n/a | 25.75 | 26.25 | 26.25 | 22.75 | 5.5 | 0.63 | 0.63 | 0.31 | 0.31 | 15.88 | 1.13 | 32.88 | 32.88 | 15.81 | 2.4375 | 2.4375 | 3.5 | 3.5 | 364T | 32 | 42.88 | 3 | 3 | 0.313 | 0.81 | n/a | 23.81 | 1.5 | 42 | 0.175 | 0.175 | 21 | 48.88 | 22.81 | 33.31 | n/a | 25.81 | 26.63 | 23.06 | 7 | 0.63 | 0.31 | 15.63 | 1.38 | 34.75 | 15.81 | 2.6875 | 4
| 330B | 33 | 143T | 365T | 35.13 | 46.75 | 2.5 | 2.5 | 0.25 | 0.56 | 0.5 | 26.25 | 26.88 | 9.88 | 1.5 | 44 | 0.126 | 0.097 | 22 | 51.75 | 25 | 36.06 | 28.38 | 28.25 | 34.88 | 17.5 | 2.4375 | 5.5 | 0.63 | 0.31 | n/a | 24.75 | 17.38 | 1.13 | 4.62 | 39 | 25.74 | 30.3875 | 1.5 | 4 | 0.5 | 3.6562 | 3.5 | 3.7812 | 324T | 365T | 35.13 | 46.75 | 2.5 | 2.5 | 0.25 | 0.56 | n/a | 26.25 | 1.5 | 44 | 0.126 | 0.097 | 22 | 51.75 | 25 | 36.06 | n/a | 28.38 | 28.25 | 28.25 | 24.75 | 5.5 | 0.63 | 0.63 | 0.31 | 0.31 | 17.38 | 1.13 | 34.88 | 34.88 | 17.5 | 2.4375 | 2.4375 | 3.5 | 4 | 365T | 35.31 | 46.88 | 3 | 3 | 0.313 | 0.81 | n/a | 26.25 | 1.5 | 45 | 0.175 | 0.175 | 22.5 | 52.88 | 25.06 | 36.63 | n/a | 28.44 | 28.44 | 25.06 | 7 | 0.75 | 0.38 | 17.13 | 1.38 | 36.69 | 17.5 | 2.9375 | 4
| 365B | 36.5 | 143T | 404T | 38.69 | 51.875 | 2.5 | 2.5 | 0.25 | 0.56 | 0.5 | 29 | 30 | 11 | 1.5 | 48 | 0.126 | 0.097 | 24 | 56.875 | 27.75 | 39.63 | 31.5 | 31.13 | 37.75 | 19.25 | 2.6875 | 5.5 | 0.63 | 0.31 | n/a | 27.31 | 18.88 | 1.13 | 5.12 | 43 | 28.47 | 33.7188 | 1.5 | 4 | 0.5 | 4.0312 | 3.5 | 4.1562 | 324T | 404T | 38.69 | 51.875 | 2.5 | 2.5 | 0.25 | 0.56 | n/a | 29 | 1.5 | 48 | 0.126 | 0.097 | 24 | 56.875 | 27.75 | 39.63 | n/a | 31.5 | 31.13 | 31.13 | 27.31 | 5.5 | 0.63 | 0.63 | 0.31 | 0.31 | 18.88 | 1.13 | 37.75 | 37.75 | 19.25 | 2.6875 | 2.6875 | 4 | 4 | 404T | 38.88 | 52 | 3 | 3 | 0.313 | 0.81 | n/a | 29 | 1.5 | 49 | 0.175 | 0.175 | 24.5 | 58 | 27.81 | 40.19 | n/a | 31.56 | 31 | 27.63 | 7 | 0.75 | 0.38 | 18.63 | 1.38 | 39.25 | 19.25 | 2.9375 | 5
TYPE C | 402B | 40.2 | 145T | 404T | 42.63 | 57.25 | 3 | 3 | 0.313 | 0.81 | 0.75 | 32 | 33.19 | 12.94 | 1.5 | 52.5 | 0.126 | 0.097 | 26.25 | 63.25 | 30.56 | 44.06 | 34.69 | 33.81 | 40.94 | 21.25 | 2.6875 | 6 | 0.63 | 0.31 | n/a | 30.25 | 20.88 | 1.38 | 5.37 | 46.5 | 31.356 | 37.2125 | 1.75 | 4 | 0.5 | 4.0312 | 3.5 | 4.1562 | 326T | 404T | 42.63 | 57.25 | 3 | 3 | 0.313 | 0.81 | n/a | 32 | 1.5 | 52.5 | 0.126 | 0.097 | 26.25 | 63.25 | 30.56 | 44.06 | n/a | 34.69 | 33.5 | 33.81 | 30.25 | 6 | 0.63 | 0.63 | 0.31 | 0.31 | 20.88 | 1.38 | 40.63 | 40.94 | 21.25 | 2.4375 | 2.6875 | 4 | 4 | 404T | 42.81 | 57.38 | 3 | 4 | 0.313 | 0.81 | n/a | 32 | 2 | 52.5 | 0.175 | 0.175 | 26.25 | 65.38 | 30.63 | 44.63 | n/a | 34.75 | 35.06 | 30.81 | 8 | 0.88 | 0.44 | 20.38 | 1.88 | 44.38 | 21.25 | 3.4375 | 5
| 445B | 44.5 | 182T | 405T | 47.13 | 63.125 | 3 | 3 | 0.313 | 0.81 | 0.75 | 35.38 | 36.75 | 14.5 | 1.5 | 56.5 | 0.126 | 0.097 | 28.25 | 69.125 | 33.75 | 48.56 | 38.25 | 36.56 | 43.81 | 23.5 | 2.9375 | 6 | 0.75 | 0.38 | n/a | 33.19 | 22.88 | 1.38 | 5.37 | 50.5 | 34.71 | 41.0312 | 1.75 | 5 | 0.5 | 4.4062 | 4.5 | 4.5312 | 364T | 405T | 47.13 | 63.125 | 3 | 3 | 0.313 | 0.81 | n/a | 35.38 | 1.5 | 56.5 | 0.126 | 0.097 | 28.25 | 69.125 | 33.75 | 48.56 | n/a | 38.25 | 36.44 | 36.56 | 33.19 | 6 | 0.63 | 0.75 | 0.31 | 0.38 | 22.88 | 1.38 | 43.56 | 43.81 | 23.5 | 2.4375 | 2.9375 | 4 | 5 | 405T | 47.31 | 63.25 | 3 | 4 | 0.313 | 0.81 | n/a | 35.38 | 2 | 56.5 | 0.175 | 0.175 | 28.25 | 71.25 | 33.81 | 49.13 | n/a | 38.31 | 38 | 33.75 | 8 | 0.88 | 0.44 | 22.38 | 1.88 | 47.31 | 23.5 | 3.4375 | 5
| 490B | 49 | 182T | 445T | 51.94 | 69.5 | 3 | 3 | 0.313 | 0.81 | 0.75 | 39 | 40.69 | 15.94 | 2 | 61.5 | 0.126 | 0.097 | 30.75 | 75.5 | 37.19 | 52.88 | 42.19 | 41.13 | 49.44 | 25.88 | 3.4375 | 7 | 0.88 | 0.44 | n/a | 36.38 | 25.38 | 1.38 | 5.37 | 55.5 | 38.22 | 45.175 | 1.75 | 5 | 0.5 | 5.1562 | 4.5 | 5.2812 | 365T | 445T | 51.94 | 69.5 | 3 | 3 | 0.313 | 0.81 | n/a | 39 | 2 | 61.5 | 0.126 | 0.097 | 30.75 | 75.5 | 37.19 | 52.88 | n/a | 42.19 | 39.94 | 41.13 | 36.38 | 7 | 0.63 | 0.88 | 0.31 | 0.44 | 25.38 | 1.38 | 48.06 | 49.44 | 25.88 | 2.6875 | 3.4375 | 4 | 5 | 445T | 52.13 | 69.63 | 3 | 4 | 0.313 | 0.81 | n/a | 39 | 2 | 61.5 | 0.175 | 0.175 | 30.75 | 77.63 | 37.25 | 53.94 | n/a | 42.25 | 41.94 | 36.94 | 9 | 1 | 0.5 | 24.88 | 1.88 | 52.31 | 25.88 | 3.9375 | 6
| 542B | 54.2 | 254T | 445T | 57.38 | 77 | 3 | 4 | 0.313 | 0.81 | 0.75 | 43.06 | 45.19 | 17.69 | 2 | 67 | 0.126 | 0.097 | 33.5 | 85 | 41.19 | 59.31 | 46.69 | 44.19 | 51.5 | 28.63 | 3.4375 | 6 | 0.88 | 0.44 | n/a | 40.63 | 27.63 | 1.88 | 5.87 | 61 | 42.276 | 50.05 | 1.75 | 5 | 0.5 | 5.1562 | 4.5 | 5.2812 | 404T | 445T | 57.38 | 77 | 3 | 4 | 0.313 | 0.81 | n/a | 43.06 | 2 | 67 | 0.126 | 0.097 | 33.5 | 85 | 41.19 | 59.31 | n/a | 46.69 | 43.75 | 44.19 | 40.63 | 6 | 0.75 | 0.88 | 0.38 | 0.44 | 27.63 | 1.88 | 51 | 51.5 | 28.63 | 2.9375 | 3.4375 | 4 | 5 | 445T | 57.56 | 77.13 | 3.5 | 5 | 0.5 | 0.81 | n/a | 43.06 | 2.5 | 67 | 0.175 | 0.175 | 33.5 | 87.13 | 41.25 | 59.88 | n/a | 46.75 | 45.69 | 41.19 | 9 | 1 | 0.5 | 27.13 | 2.38 | 56.06 | 28.63 | 3.9375 | 6
| 600B | 60 | 254T | 445T | 63.5 | 85 | 3 | 4 | 0.313 | 0.81 | 0.75 | 47.69 | 50.19 | 19.69 | 2 | 73 | 0.126 | 0.097 | 36.5 | 93 | 45.56 | 65.44 | 51.69 | 49.63 | 59 | 31.69 | 3.9375 | 8 | 1 | 0.5 | n/a | 44.63 | 30.63 | 1.88 | 5.87 | 67 | 46.8 | 55.25 | 2 | 6 | 0.5 | 5.9062 | 5.5 | 6.0312 | 405T | 445T | 63.5 | 85 | 3 | 4 | 0.313 | 0.81 | n/a | 47.69 | 2 | 73 | 0.126 | 0.097 | 36.5 | 93 | 45.56 | 65.44 | n/a | 51.69 | 48.88 | 49.63 | 44.63 | 8 | 0.88 | 1 | 0.44 | 0.5 | 30.63 | 1.88 | 58.19 | 59 | 31.69 | 3.4375 | 3.9375 | 5 | 6 | 445T | 63.69 | 85.13 | 3.5 | 5 | 0.5 | 0.81 | n/a | 47.69 | 2.5 | 74 | 0.175 | 0.175 | 37 | 95.13 | 45.63 | 66 | n/a | 51.75 | 50.44 | 45.19 | 9.5 | 1 | 0.5 | 30.13 | 2.38 | 61.31 | 31.69 | 4.4375 | 7
| 660B | 66 | 254T | 445T | 69.69 | 93.75 | 3.5 | 5 | 0.5 | 0.81 | 0.75 | 52.44 | 55.31 | 22.31 | 2.5 | 80 | 0.126 | 0.097 | 40 | 103.75 | 49.94 | 72.13 | 56.81 | 54.06 | 63.38 | 34.75 | 3.9375 | 8 | 1 | 0.5 | n/a | 49.5 | 33.13 | 2.38 | 6.87 | 73 | 51.48 | 60.9375 | 2 | 6 | 0.5 | 5.9062 | 5.5 | 6.0312 | 405T | 445T | 69.69 | 93.75 | 3.5 | 5 | 0.5 | 0.81 | n/a | 52.44 | 2.5 | 80 | 0.126 | 0.097 | 40 | 103.75 | 49.94 | 72.13 | n/a | 56.81 | 53.25 | 54.06 | 49.5 | 8 | 0.88 | 1 | 0.44 | 0.5 | 33.13 | 2.38 | 62.56 | 63.38 | 34.75 | 3.4375 | 3.9375 | 5 | 6 | 445T | 69.88 | 93.88 | 4 | 6 | 0.5 | 0.81 | n/a | 52.44 | 2.5 | 80 | 0.175 | 0.175 | 40 | 105.88 | 50 | 73.19 | n/a | 56.88 | 55.12 | 50.06 | 10 | 1.25 | 0.63 | 32.63 | 2.88 | 66.63 | 34.75 | 4.9375 | 7
| 730B | 73 | 254T | 445T | 77.25 | 103.375 | 3.5 | 5 | 0.5 | 0.81 | 0.75 | 58 | 61.38 | 24.38 | 2.5 | 88 | 0.126 | 0.126 | 44 | 113.375 | 55.38 | 79.63 | 62.88 | 58.81 | 69.19 | 38.5 | 3.9375 | 9 | 1 | 0.5 | n/a | 54.31 | 37.13 | 2.38 | 6.87 | 81 | 56.94 | 67.1938 | 2 | 6 | 0.5 | 5.9062 | 5.5 | 6.0312 | 445T | 445T | 77.25 | 103.375 | 3.5 | 5 | 0.5 | 0.81 | n/a | 58 | 2.5 | 88 | 0.126 | 0.126 | 44 | 113.375 | 55.38 | 79.63 | n/a | 62.88 | 58.81 | 58.81 | 54.31 | 9 | 1 | 1 | 0.5 | 0.5 | 37.13 | 2.38 | 69.19 | 69.19 | 38.5 | 3.9375 | 3.9375 | 6 | 6 | 445T | 77.38 | 103.5 | 4 | 6 | 0.5 | 0.81 | n/a | 58 | 2.5 | 88 | 0.175 | 0.175 | 44 | 115.5 | 55.44 | 80.69 | n/a | 62.94 | 59.94 | 54.88 | 10 | 1.25 | 0.63 | 36.63 | 2.88 | 71.44 | 38.5 | 4.9375 | 7

## Load Calculations
Total Load
COG Calculations
| Total Load S1 | Total Load S2 | Total Load S3 | Total Load S4 | Base_Z | 43.61
| 384 | 773 | 470 | 478 | Base_X | 87.0306
| Iso S1 | Iso S2 | Iso S3 | Iso S4 | Fan_Z1 | 19.81
[5 empty] | Fan_Z2 | 23.8
| 029 23800 111 | 029 23800 104 | 029 23800 103 | 029 23800 103 | Fan_X1 | 58.4002
| Iso Plate S1 | Iso Plate S2 | Iso Plate S3 | Iso Plate S4 | Fan_X2 | 28.6304
[5 empty] | Motor_Z1 | 35.69
| 391 20112 103 | 391 20112 101 | 391 20112 103 | 391 20112 101 | Motor_Z2 | 7.92
QTY: | 1 | 1 | 1 | 1 | Motor_X1 | 12.8952
[5 empty] | Motor_X2 | 74.1354
[5 empty] | MotorBase_Z1 | 35.69
[5 empty] | MotorBase_Z2 | 7.92
Individual Component Loads |  |  |  |  | MotorBase_X1 | 12.8952
| PERIMETER STEEL |  |  |  | MotorBase_X2 | 74.1354
| PerSteel S1 | PerSteel S2 | PerSteel S3 | PerSteel S4 | IntFanRail_DOA_Z1 | 21.805
| 53.611 | 53.611 | 53.611 | 53.611 | IntFanRail_DOA_Z2 | 21.805
| FAN |  |  |  | IntFanRail_DOA_X1 | 35.8206
| Fan S1 | Fan S2 | Fan S3 | Fan S4 | IntFanRail_DOA_X2 | 51.21
| 188.331 | 156.7579 | 384.157 | 319.7542 | IntMtrRail_DOA_Z1 | 21.805
| MOTOR |  |  |  | IntMtrRail_DOA_Z2 | 21.805
| Motor S1 | Motor S2 | Motor S3 | Motor S4 | IntMtrRail_DOA_X1 | 20.8556
| 112.1581 | 505.4197 | 19.5089 | 87.9133 | IntMtrRail_DOA_X2 | 66.175
| MOTOR BASE |  |  |  | IntRail_DOW_Z1 | 0
| MtrBase S1 | MtrBase S2 | MtrBase S3 | MtrBase S4 | IntRail_DOW_Z2 | 0
| 4.7957 | 21.611 | 0.83417 | 3.7591 | IntRail_DOW_X1 | 0
| INTERNAL FAN RAIL DIRECTION OF AIRFLOW |  |  |  | IntRail_DOW_X2 | 0
| IntFanRail DOA S1 | IntFanRail DOA S2 | IntFanRail DOA S3 | IntFanRail DOA S4 | MotorSupRail1_Z1 | 43.69
| 9.6037 | 9.6037 | 6.7177 | 6.7177 | MotorSupRail1_Z2 | -0.08
| INTERNAL MTR RAIL DIRECTION OF AIRFLOW |  |  |  | MotorSupRail1_X1 | 12.8952
| IntMtrRail DOA S1 | IntMtrRail DOA S2 | IntMtrRail DOA S3 | IntMtrRail DOA S4 | MotorSupRail1_X2 | 74.1354
| 12.4102 | 12.4102 | 3.9112 | 3.9112 | MotorSupRail2_Z1 | 27.69
| INTERNAL RAIL DIRECTION OF WIDTH |  |  |  | MotorSupRail2_Z2 | 15.92
| IntRail DOW S1 | IntRail DOW S2 | IntRail DOW S3 | IntRail DOW S4 | MotorSupRail2_X1 | 12.8952
| 0 | 0 | 0 | 0 | MotorSupRail2_X2 | 74.1354
| MOTOR SUPPORT RAIL 1 |  |  |  | InertiaPlate_Zone1_Z1 | 21.805
| MtrSup1 S1 | MtrSup1 S2 | MtrSup1 S3 | MtrSup1 S4 | InertiaPlate_Zone1_Z2 | 21.805
| -0.014943 | 8.1606 | -0.0025992 | 1.4195 | InertiaPlate_Zone1_X1 | 43.5153
| MOTOR SUPPORT RAIL 2 |  |  |  | InertiaPlate_Zone1_X2 | 43.5153
| MtrSup2 S1 | MtrSup2 S2 | MtrSup2 S3 | MtrSup2 S4 | InertiaPlate_Zone2_Z1 | 21.805
| 2.9736 | 5.172 | 0.51723 | 0.89963 | InertiaPlate_Zone2_Z2 | 21.805
| INERTIA PLATE ZONE 1 WEIGHT ADD |  |  |  | InertiaPlate_Zone2_X1 | 69.7806
| Plate1 S1 | Plate1 S2 | Plate1 S3 | Plate1 S4 | InertiaPlate_Zone2_X2 | 17.25
| 0 | 0 | 0 | 0 | InertiaRebar_Zone1_Z1 | 21.805
| INERTIA PLATE ZONE 2 WEIGHT ADD |  |  |  | InertiaRebar_Zone1_Z2 | 21.805
| Plate2 S1 | Plate2 S2 | Plate2 S3 | Plate2 S4 | InertiaRebar_Zone1_X1 | 43.5153
| 0 | 0 | 0 | 0 | InertiaRebar_Zone1_X2 | 43.5153
| INERTIA REBAR ZONE 1 WEIGHT ADD |  |  |  | InertiaRebar_Zone2_Z1 | 21.805
| Rebar1 S1 | Rebar1 S2 | Rebar1 S3 | Rebar1 S4 | InertiaRebar_Zone2_Z2 | 21.805
| 0 | 0 | 0 | 0 | InertiaRebar_Zone2_X1 | 43.5153
| INERTIA REBAR ZONE 2 WEIGHT ADD |  |  |  | InertiaRebar_Zone2_X2 | 43.5153
| Rebar2 S1 | Rebar2 S2 | Rebar2 S3 | Rebar2 S4 | InertiaConcrete_Zone1_Z1 | 21.805
| 0 | 0 | 0 | 0 | InertiaConcrete_Zone1_Z2 | 21.805
| INERTIA CONCRETE ZONE 1 WEIGHT ADD |  |  |  | InertiaConcrete_Zone1_X1 | 43.5153
| Concrete1 S1 | Concrete1 S2 | Concrete1 S3 | Concrete1 S4 | InertiaConcrete_Zone1_X2 | 43.5153
| 0 | 0 | 0 | 0 | InertiaConcrete_Zone2_Z1 | 21.805
| INERTIA CONCRETE ZONE 2 WEIGHT ADD |  |  |  | InertiaConcrete_Zone2_Z2 | 21.805
| Concrete2 S1 | Concrete2 S2 | Concrete2 S3 | Concrete2 S4 | InertiaConcrete_Zone2_X1 | 43.5153
| 0 | 0 | 0 | 0 | InertiaConcrete_Zone2_X2 | 43.5153
Weight Values
[5 empty] | Perimeter Steel | 214.4442 | lb.
[5 empty] | Fan | 1049 | lb.
[5 empty] | Motor | 725 | lb.
[5 empty] | Motor Base | 31 | lb.
[5 empty] | Internal Fan Rail DOA | 32.6428 | lb.
[5 empty] | Internal Mtr Rail DOA | 32.6428 | lb.
[5 empty] | Internal Rail DOW | 0 | lb.
[5 empty] | Motor Support Rail | 9.5625 | lb.
[5 empty] | Inertia Plate Weight Total Zone1 | 0 | lb.
[5 empty] | Inertia Plate Weight Total Zone2 | 0 | lb.
[5 empty] | Rebar Weight Total Zone1 | 0 | lb.
[5 empty] | Rebar Weight Total Zone2 | 0 | lb.
[5 empty] | Concrete Weight Total Zone1 | 0 | lb.
[5 empty] | Concrete Weight Total Zone2 | 0 | lb.
General assumptions used for calculations:
1. For all non bottom discharge fans, the Perimeter Steel, Inertia bottom plates, Inertia rebar, & Inertia concrete are all considered as a single unit with the COG the midplanes between the isolator holes. (Total weight is equally distributed to the 4 isolators) For all bottom discharge arrangements only Perimeter Steel is equally distributed, Inertia bottom plates, Inertia rebar, & Inertia concrete are seperated into 2 zones and weight is distributed accordingly. (See pictures tied to COG calculations to left for zone layouts)
2. COG of all Internal Rails is assumed to be the intersection of the midplane in length and centerline in flange direction.
3. COG of Motor Support Rails is assumed to be the intersection of the midplanes in length and height.
4. COG of Fan is assumed to be the intersection of the shaft centerline and the fan discharge centerline.
Fan sheave estimated weight is added to total fan weight.
5. COG of Motor is assumed to be the intersection of the shaft centerline and the midpoint between the mounting holes. Motor sheave estimated weight is added to total motor weight
6. COG of Motor Base is assumed to be the intersection of midplanes between mounting holes.
7. Weight calculations for sheaves are just a general estimate based on HP of motor. (Motor HP/2)
8. All dimensions (X1, X2, Z1, Z2) are to the assumed COG of the various components.
W = the weight of the component being calculated.

## Center Distance
CENTER DISTANCE CALCULATIONS
A_MTR | 12.416
B_MTR_Default | 15.88
B_MTR_Over_Max_Angle | 15.88
C_MTR_MidPoint | 20.1577
C_MTR_MIN | 18.8883
C_MTR_MAX | 21.427
B_Total_Used_ADJ_Length | 2
C_Total_Used_ADJ_Length | 2.5387
B_Total_MtrBase_ADJ_Length | 5.25
C_Total_MtrBase_ADJ_Length | 6.6642
D_Calculated_Angle | 38.0206
D_Max_Angle | 45
CENTER DISTANCE OUTPUTS
CENTER_DISTANCE_MIN | 18.8883
CENTER_DISTANCE_MAX | 21.427
SHAFT DIAMETERS
MOTOR_SHAFT_DIAMETER | 2.125
FAN_SHAFT_DIAMETER | 2.4375

## Channel Loc
CHANNEL LOCATION DIMENSIONS (Z_LOCATION) FROM PRIMARY_Z_PLANE (SEGMENT START)
Channel Name | Z_LOCATION | X_ARRAY_OFFSET | X_ARRAY_QTY | X_ARRAY_SPACING | FLOOR CHANNELS
FLOOR_CHAN_1 | 24.89 | 0 | 0 | 0 |  | FIA SPRING LOC | Z - Location information only used if steel is oriented across the width of the unit.
FLOOR_CHAN_2 | 68.5 | 0 | 0 | 0 |  | LIA SPRING LOC
FLOOR_CHAN_3 | 0 | 19.2146 | 0 | 0 |  | RH SPRING LOC | X - Location information only used if steel is oriented in direction of airflow.
FLOOR_CHAN_4 | 0 | 106.2452 | 0 | 0 |  | LH SPRING LOC
FLOOR_CHAN_5 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_6 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_7 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_8 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_9 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_10 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_11 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_12 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_13 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_14 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_15 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_16 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_17 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_18 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_19 | 0 | 0 | 0 | 0 |  | NOT USED
FLOOR_CHAN_20 | 0 | 0 | 0 | 0 |  | NOT USED
Channel Name | Z_LOCATION | X_ARRAY_OFFSET | X_ARRAY_QTY | X_ARRAY_SPACING | ROOF CHANNELS
ROOF_CHAN_1 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_2 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_3 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_4 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_5 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_6 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_7 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_8 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_9 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_10 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_11 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_12 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_13 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_14 | 0 | 0 | 0 | 0 |  | NOT USED
ROOF_CHAN_15 | 0 | 0 | 0 | 0 |  | NOT USED
Channel Name | Z_LOCATION | Y_ARRAY_OFFSET | Y_ARRAY_QTY | Y_ARRAY_SPACING | NORTH WALL CHANNELS
RIGHT_HAND_CHAN_1 | 0 | 0 | 0 | 0 |  | NOT USED
RIGHT_HAND_CHAN_2 | 0 | 0 | 0 | 0 |  | NOT USED
RIGHT_HAND_CHAN_3 | 0 | 0 | 0 | 0 |  | NOT USED
RIGHT_HAND_CHAN_4 | 0 | 0 | 0 | 0 |  | NOT USED
RIGHT_HAND_CHAN_5 | 0 | 0 | 0 | 0 |  | NOT USED
RIGHT_HAND_CHAN_6 | 0 | 0 | 0 | 0 |  | NOT USED
RIGHT_HAND_CHAN_7 | 0 | 0 | 0 | 0 |  | NOT USED
RIGHT_HAND_CHAN_8 | 0 | 0 | 0 | 0 |  | NOT USED
RIGHT_HAND_CHAN_9 | 0 | 0 | 0 | 0 |  | NOT USED
RIGHT_HAND_CHAN_10 | 0 | 0 | 0 | 0 |  | NOT USED
Channel Name | Z_LOCATION | Y_ARRAY_OFFSET | Y_ARRAY_QTY | Y_ARRAY_SPACING | SOUTH WALL CHANNELS
LEFT_HAND_CHAN_1 | 0 | 0 | 0 | 0 |  | NOT USED
LEFT_HAND_CHAN_2 | 0 | 0 | 0 | 0 |  | NOT USED
LEFT_HAND_CHAN_3 | 0 | 0 | 0 | 0 |  | NOT USED
LEFT_HAND_CHAN_4 | 0 | 0 | 0 | 0 |  | NOT USED
LEFT_HAND_CHAN_5 | 0 | 0 | 0 | 0 |  | NOT USED
LEFT_HAND_CHAN_6 | 0 | 0 | 0 | 0 |  | NOT USED
LEFT_HAND_CHAN_7 | 0 | 0 | 0 | 0 |  | NOT USED
LEFT_HAND_CHAN_8 | 0 | 0 | 0 | 0 |  | NOT USED
LEFT_HAND_CHAN_9 | 0 | 0 | 0 | 0 |  | NOT USED
LEFT_HAND_CHAN_10 | 0 | 0 | 0 | 0 |  | NOT USED

## Motor Base
MTRBS_FRAME | MTRBS_AL | MTRBS_AM | MTRBS_AX | MTRBS_BB | MTRBS_BT | MTRBS_E | MTRBS_F | MTRBS_AO | MTRBS_AR | MTRBS_AU | MTRBS_AT | MTRBS_XC | MTRBS_DBOLT_D | MTRBS_DBOLT_L | MTRBS_AYBOLT_D | MTRBS_AYBOLT_L | MTRBS_LB
56 | 10.625 | 6.5 | 1.125 | 4.5 | 3 | 2.4375 | 1.5 | 3.8125 | 2.875 | 0.375 | 0.078 | 0.875 | 0.3125 | 1 | 0.375 | 4 | 3
143T | 10.5 | 7.5 | 1.125 | 5.5 | 3 | 2.75 | 2 | 3.75 | 3.375 | 0.375 | 0.119 | 0.8125 | 0.3125 | 1 | 0.375 | 4 | 5
145T | 10.5 | 8.5 | 1.125 | 6.5 | 3 | 2.75 | 2.5 | 3.75 | 3.875 | 0.375 | 0.119 | 0.8125 | 0.3125 | 1 | 0.375 | 4 | 6
182T | 12.75 | 9.5 | 1.5 | 6.5 | 3 | 3.75 | 2.25 | 4.5 | 4.25 | 0.5 | 0.134 | 1.5 | 0.375 | 1.75 | 0.5 | 6 | 9
184T | 12.75 | 10.5 | 1.5 | 7.5 | 3 | 3.75 | 2.75 | 4.5 | 4.75 | 0.5 | 0.134 | 1.5 | 0.375 | 1.75 | 0.5 | 6 | 9.5
213T | 15 | 11 | 1.75 | 7.5 | 3.5 | 4.25 | 2.75 | 5.25 | 4.75 | 0.5 | 0.164 | 1.5 | 0.375 | 1.75 | 0.5 | 6 | 13.5
215T | 15 | 12.5 | 1.75 | 9 | 3.5 | 4.25 | 3.5 | 5.25 | 5.5 | 0.5 | 0.164 | 1.5 | 0.375 | 1.75 | 0.5 | 6 | 15.5
254T | 17.75 | 15.125 | 2 | 10.75 | 4 | 5 | 4.125 | 6.25 | 6.625 | 0.625 | 0.1875 | 1.375 | 0.5 | 1.75 | 0.625 | 9 | 17
256T | 17.75 | 16.875 | 2 | 12.5 | 4 | 5 | 5 | 6.25 | 7.5 | 0.625 | 0.1875 | 1.375 | 0.5 | 1.75 | 0.625 | 9 | 18
284T | 19.75 | 16.875 | 2 | 12.5 | 4.5 | 5.5 | 4.75 | 7 | 7.5 | 0.625 | 0.1875 | 1.625 | 0.5 | 2 | 0.625 | 9 | 21
286T | 19.75 | 18.375 | 2 | 14 | 4.5 | 5.5 | 5.5 | 7 | 8.25 | 0.625 | 0.1875 | 1.625 | 0.5 | 2 | 0.625 | 9 | 22
324T | 22.75 | 19.25 | 2.5 | 14 | 5.25 | 6.25 | 5.25 | 8 | 8.5 | 0.75 | 0.1875 | 2.125 | 0.625 | 2.5 | 0.75 | 9 | 30
326T | 22.75 | 20.75 | 2.5 | 15.5 | 5.25 | 6.25 | 6 | 8 | 9.25 | 0.75 | 0.1875 | 2.125 | 0.625 | 2.5 | 0.75 | 9 | 31
364T | 25.5 | 20.5 | 2.5 | 15.5 | 6 | 7 | 5.625 | 9 | 9.125 | 0.75 | 0.25 | 2 | 0.625 | 2.5 | 0.75 | 11 | 45
365T | 25.5 | 21.5 | 2.5 | 16.5 | 6 | 7 | 6.125 | 9 | 9.625 | 0.75 | 0.25 | 2 | 0.625 | 2.5 | 0.75 | 11 | 46
404T | 28.75 | 22.375 | 3 | 16.5 | 7 | 8 | 6.125 | 10 | 9.875 | 0.875 | 0.25 | 2.5625 | 0.75 | 3 | 0.75 | 14 | 55
405T | 28.75 | 23.875 | 3 | 18 | 7 | 8 | 6.875 | 10 | 10.625 | 0.875 | 0.25 | 2.5625 | 0.75 | 3 | 0.75 | 14 | 56
444T | 31.25 | 24.625 | 3 | 19.25 | 7.5 | 9 | 7.25 | 11 | 11 | 0.875 | 0.3125 | 2.5 | 0.75 | 3 | 0.75 | 14 | 74
445T | 31.25 | 26.625 | 3 | 21.25 | 7.5 | 9 | 8.25 | 11 | 12 | 0.875 | 0.3125 | 2.5 | 0.75 | 3 | 0.75 | 14 | 75
447T | 31.25 | 30.125 | 3 | 24.75 | 7.5 | 9 | 10 | 11 | 13.75 | 0.875 | 0.3125 | 2.5 | 0.75 | 3 | 0.75 | 14 | 89
449T | 31.25 | 35.125 | 3 | 29.75 | 7.5 | 9 | 12.5 | 11 | 16.25 | 0.875 | 0.3125 | 2.5 | 0.75 | 3 | 0.75 | 14 | 95

## Hardware
Hardware Nominal Hole Dia | Hardware Description | Bolt Outside Diameter | Hex Nut Heavy Height/Thickness | Hex Nut Heavy Outside Diameter | Hex Nut Heavy Height/Thickness | Flat Washer (ANSI A Narrow) Outside Diameter | Helical Spring Lock Washer (ANSI Regular) Outside Diameter
HDWR_NHD |  | HDWR_BOD | HDWR_BH | HDWR_NOD | HDWR_NH | HDWR_FWOD | HDWR_LWOD
0.375 | 5/16-18 UNC | 0.578 | 0.235 | 0.651 | 0.297 | 0.688 | 0.586
0.5 | 3/8-16 UNC | 0.649 | 0.268 | 0.795 | 0.359 | 0.812 | 0.683
0.625 | 1/2-13 UNC | 0.866 | 0.364 | 1.01 | 0.484 | 1.062 | 0.873
0.75 | 5/8-11 UNC | 1.083 | 0.444 | 1.23 | 0.609 | 1.312 | 1.079
0.875 | 3/4-10 UNC | 1.299 | 0.524 | 1.44 | 0.734 | 1.469 | 1.271

## Motor
MTR_FRAME | MTR_C | MTR_D | MTR_E | MTR_2F | MTR_H | MTR_P | MTR_KWL | MTR_R | MTR_S | MTR_U | MTR_V | MTR_AB | MTR_BA | MTR_BL | MTR_BW | MTR_D1 | MTR_D2 | MTR_HP
56 | 15.48 | 3.5 | 2.44 | 3 | 0.344 | 6.625 | 1.375 | 0.516 | 0.188 | 0.625 | 1.875 | 5.72 | 2.75 | 4.5 | 6.5 | 0.75 | 0.19 | 1
143T | 15.56 | 3.5 | 2.75 | 4 | 0.34375 | 6.625 | 1.375 | 0.766 | 0.188 | 0.875 | 2.25 | 6.38 | 2.25 | 5.94 | 6.5 | 0.5 | 0.19 | 1.5
145T | 15.56 | 3.5 | 2.75 | 5 | 0.34375 | 6.625 | 1.375 | 0.766 | 0.188 | 0.875 | 2.25 | 6.38 | 2.25 | 5.94 | 6.5 | 0.5 | 0.19 | 2
182T | 18.05 | 4.5 | 3.75 | 4.5 | 0.41 | 7.875 | 1.75 | 0.984 | 0.25 | 1.125 | 2.75 | 7.18 | 2.75 | 6.5 | 8.63 | 0.5 | 0.56 | 3
184T | 18.05 | 4.5 | 3.75 | 5.5 | 0.41 | 7.875 | 1.75 | 0.984 | 0.25 | 1.125 | 2.75 | 7.18 | 2.75 | 6.5 | 8.63 | 0.5 | 0.56 | 5
213T | 20.51 | 5.25 | 4.25 | 5.5 | 0.41 | 9.563 | 2.375 | 1.203 | 0.313 | 1.375 | 3.375 | 9.21 | 3.5 | 8 | 9.5 | 0.5 | 0.465 | 7.5
215T | 20.51 | 5.25 | 4.25 | 7 | 0.41 | 9.563 | 2.375 | 1.203 | 0.313 | 1.375 | 3.375 | 9.21 | 3.5 | 8 | 9.5 | 0.5 | 0.465 | 10
254T | 23.28 | 6.25 | 5 | 8.25 | 0.531 | 12.938 | 2.875 | 1.406 | 0.375 | 1.625 | 4 | 10.04 | 4.25 | 11.5 | 11.5 | 0.75 | 0.38 | 15
256T | 23.28 | 6.25 | 5 | 10 | 0.531 | 12.938 | 2.875 | 1.406 | 0.375 | 1.625 | 4 | 10.04 | 4.25 | 11.5 | 11.5 | 0.75 | 0.38 | 20
284T | 27.76 | 7 | 5.5 | 9.5 | 0.531 | 14.625 | 3.25 | 1.594 | 0.5 | 1.875 | 4.625 | 13.11 | 4.75 | 12.84 | 12.75 | 0.92 | 0.39 | 25
286T | 27.76 | 7 | 5.5 | 11 | 0.531 | 14.625 | 3.25 | 1.594 | 0.5 | 1.875 | 4.625 | 13.11 | 4.75 | 12.84 | 12.75 | 0.92 | 0.39 | 30
324T | 30.28 | 8 | 6.25 | 10.5 | 0.656 | 16.5 | 3.875 | 1.844 | 0.5 | 2.125 | 5.25 | 14.61 | 5.25 | 14 | 14.5 | 1 | 0.44 | 40
326T | 30.28 | 8 | 6.25 | 12 | 0.656 | 16.5 | 3.875 | 1.844 | 0.5 | 2.125 | 5.25 | 14.61 | 5.25 | 14 | 14.5 | 1 | 0.44 | 50
364T | 33.48 | 9 | 7 | 11.25 | 0.656 | 19.5 | 4.25 | 2.016 | 0.625 | 2.375 | 5.875 | 18.1 | 5.875 | 15 | 17 | 1.375 | 0 | 60
365T | 33.48 | 9 | 7 | 12.25 | 0.656 | 19.5 | 4.25 | 2.016 | 0.625 | 2.375 | 5.875 | 18.1 | 5.875 | 15 | 17 | 1.375 | 0 | 75
404T | 38.2 | 10 | 8 | 12.25 | 0.813 | 22.5 | 5.625 | 2.453 | 0.75 | 2.875 | 7.25 | 19.35 | 6.625 | 16 | 19 | 1.125 | 0 | 100
405T | 38.2 | 10 | 8 | 13.75 | 0.813 | 22.5 | 5.625 | 2.453 | 0.75 | 2.875 | 7.25 | 19.35 | 6.625 | 16 | 19 | 1.125 | 0 | 125
444T | 44.75 | 11 | 9 | 14.5 | 0.813 | 28.75 | 6.875 | 2.875 | 0.875 | 3.375 | 8.375 | 22.68 | 7.5 | 23.375 | 22 | 3.438 | 0 | 200
445T | 44.75 | 11 | 9 | 16.5 | 0.813 | 28.75 | 6.875 | 2.875 | 0.875 | 3.375 | 8.375 | 22.68 | 7.5 | 23.375 | 22 | 3.438 | 0 | 250
KWL
Keyway length
TEFC
BL
BW
D1
D2
The "C" dimension on a TEFC motor is larger, than the "C" dimension on an ODP motor.
Table dimensions are based on TEFC as a worst case scenario

## Isolator Plate
|  | Plate Designation | Plate | Plate Part Numer | All Thread Part Number | Plate Asy Part Number (Plate & 3/4-10x3 All-Thread Stubs) | Plate Width | Plate Length | Plate Thickness | Plate Hole Dia | Spring Hole Dia | Offset Suppresion | Standard Suppresion | Spring CL Width Loc | Spring Width Loc 1 | Spring Width Loc 2 | Spring CL Length Loc | Spring Length Loc 1 | Spring Length Loc 2
|  | PLT_D |  |  |  | PLT_PN | PLT_W | PLT_L | PLT_T | PLT_PH | PLT_SH | PLT_OS | PLT_SS | PLT_SWI | PLT_SW1 | PLT_SW2 | PLT_SLI | PLT_SL1 | PLT_SL2
BASELINE | STL GALV | 1 | AMSR-1C STANDARD | 391 25726 100 | 021-19602-000 | 391 20112 105 | 9 | 13 | 0.15601 | 0.25 | 0.5 | NO | YES | 3 | 2.25 | 3.75 | 6.5 | 4.25 | 8.75
BASELINE | STL GALV | 2 | AMSR-1C OFFSET | 391 25728 100 | 021-19602-000 | 391 20112 106 | 9 | 13 | 0.15601 | 0.25 | 0.5 | YES | NO | 4.5 | 3.75 | 5.25 | 3.8125 | 1.5625 | 6.0625
BASELINE | STL GALV | 3 | AMSR-2D STANDARD | 391 25726 000 | 021-19601-000 | 391 20112 101 | 9 | 13 | 0.15601 | 0.25 | 0.75 | NO | YES | 3 | 1.125 | 4.875 | 6.5 | 3.8125 | 9.1875
BASELINE | STL GALV | 4 | AMSR-2D OFFSET | 391 25728 000 | 021-19601-000 | 391 20112 103 | 9 | 13 | 0.15601 | 0.25 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 3.8125 | 1.125 | 6.5
BASELINE | STL GALV | 5 | AMSR-2E STANDARD | 391 25727 000 | 021-19601-000 | 391 20112 102 | 9 | 13 | 0.15601 | 0.25 | 0.75 | NO | YES | 3 | 1.125 | 4.875 | 6.5 | 3.125 | 9.875
BASELINE | STL GALV | 6 | AMSR-2E OFFSET | 391 25729 000 | 021-19601-000 | 391 20112 104 | 9 | 13 | 0.15601 | 0.25 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 4.5 | 1.125 | 7.875
BASELINE | STL GALV | 7 | AMSR-1C OFFSET SM | 391-25728-101 | 021-19602-000 | 391 20112 107 | 9 | 8.92 | 0.15601 | 0.25 | 0.5 | YES | NO | 4.5 | 3.75 | 5.25 | 3.813 | 1.563 | 6.063
BASELINE | STL GALV | 8 | AMSR-2D OFFSET SM | 391-25728-102 | 021-19601-000 | 391 20112 108 | 9 | 8.92 | 0.15601 | 0.25 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 3.813 | 1.125 | 6.5
BASELINE | SST304 | 1 | AMSR-1C STANDARD | 091-01110-001 | 021-37034-001 | 391-01106-001 | 9 | 13 | 0.16501 | 0.25 | 0.5 | NO | YES | 3 | 2.25 | 3.75 | 6.5 | 4.25 | 8.75
BASELINE | SST304 | 2 | AMSR-1C OFFSET | 091-01110-002 | 021-37034-001 | 391-01106-002 | 9 | 13 | 0.16501 | 0.25 | 0.5 | YES | NO | 4.5 | 3.75 | 5.25 | 3.813 | 1.563 | 6.063
BASELINE | SST304 | 3 | AMSR-2D STANDARD | 091-01110-003 | 021-37035-001 | 391-01106-003 | 9 | 13 | 0.16501 | 0.25 | 0.75 | NO | YES | 3 | 1.125 | 4.875 | 6.5 | 3.813 | 9.188
BASELINE | SST304 | 4 | AMSR-2D OFFSET | 091-01110-004 | 021-37034-001 | 391-01106-004 | 9 | 13 | 0.16501 | 0.25 | 0.5 | NO | YES | 3 | 1.125 | 4.875 | 6.5 | 3.125 | 9.875
BASELINE | SST304 | 5 | AMSR-2E STANDARD | 091-01110-005 | 021-37034-001 | 391-01106-005 | 9 | 13 | 0.16501 | 0.25 | 0.5 | YES | NO | 4.5 | 2.625 | 6.375 | 3.813 | 1.125 | 6.5
BASELINE | SST304 | 6 | AMSR-2E OFFSET | 091-01110-006 | 021-37035-001 | 391-01106-006 | 9 | 13 | 0.16501 | 0.25 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 4.5 | 1.125 | 7.875
BASELINE | SST304 | 7 | AMSR-1C OFFSET SM | 091-01110-007 | 021-37034-001 | 391-01106-007 | 9 | 8.92 | 0.16501 | 0.25 | 0.5 | YES | NO | 4.5 | 3.75 | 5.25 | 3.813 | 1.563 | 6.063
BASELINE | SST304 | 8 | AMSR-2D OFFSET SM | 091-01110-008 | 021-37035-001 | 391-01106-008 | 9 | 8.92 | 0.16501 | 0.25 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 3.813 | 1.125 | 6.5
SEISMIC | STL GALV | 1 | AMSR-1C STANDARD | 091-01095-001 | 021-19602-000 | 391-01094-001 | 9 | 13 | 0.25001 | 0.437 | 0.5 | NO | YES | 3 | 2.25 | 3.75 | 6.5 | 4.25 | 8.75
SEISMIC | STL GALV | 2 | AMSR-1C OFFSET | 091-01095-002 | 021-19602-000 | 391-01094-002 | 9 | 13 | 0.25001 | 0.437 | 0.5 | YES | NO | 4.5 | 3.75 | 5.25 | 3.8125 | 1.5625 | 6.0625
SEISMIC | STL GALV | 3 | AMSR-2D STANDARD | 091-01095-003 | 021-19601-000 | 391-01094-003 | 9 | 13 | 0.25001 | 0.437 | 0.75 | NO | YES | 3 | 1.125 | 4.875 | 6.5 | 3.8125 | 9.1875
SEISMIC | STL GALV | 4 | AMSR-2D OFFSET | 091-01095-004 | 021-19601-000 | 391-01094-004 | 9 | 13 | 0.25001 | 0.437 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 3.8125 | 1.125 | 6.5
SEISMIC | STL GALV | 5 | AMSR-2E STANDARD | 091-01095-005 | 021-19601-000 | 391-01094-005 | 9 | 13 | 0.25001 | 0.437 | 0.75 | NO | YES | 3 | 1.125 | 4.875 | 6.5 | 3.125 | 9.875
SEISMIC | STL GALV | 6 | AMSR-2E OFFSET | 091-01095-006 | 021-19601-000 | 391-01094-006 | 9 | 13 | 0.25001 | 0.437 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 4.5 | 1.125 | 7.875
SEISMIC | STL GALV | 7 | AMSR-1C OFFSET SM | 091-01095-007 | 021-19602-000 | 391-01094-007 | 9 | 8.92 | 0.25001 | 0.437 | 0.5 | YES | NO | 4.5 | 3.75 | 5.25 | 3.8125 | 1.5625 | 6.0625
SEISMIC | STL GALV | 8 | AMSR-2D OFFSET SM | 091-01095-008 | 021-19601-000 | 391-01094-008 | 9 | 8.92 | 0.25001 | 0.437 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 3.8125 | 1.125 | 6.5
SEISMIC | SST304 | 1 | AMSR-1C STANDARD | 091-01095-009 | 021-37034-001 | 391-01094-009 | 9 | 13 | 0.25002 | 0.437 | 0.5 | NO | YES | 3 | 2.25 | 3.75 | 6.5 | 4.25 | 8.75
SEISMIC | SST304 | 2 | AMSR-1C OFFSET | 091-01095-010 | 021-37034-001 | 391-01094-010 | 9 | 13 | 0.25002 | 0.437 | 0.5 | YES | NO | 4.5 | 3.75 | 5.25 | 3.8125 | 1.5625 | 6.0625
SEISMIC | SST304 | 3 | AMSR-2D STANDARD | 091-01095-011 | 021-37035-001 | 391-01094-011 | 9 | 13 | 0.25002 | 0.437 | 0.75 | NO | YES | 3 | 1.125 | 4.875 | 6.5 | 3.8125 | 9.1875
SEISMIC | SST304 | 4 | AMSR-2D OFFSET | 091-01095-012 | 021-37035-001 | 391-01094-012 | 9 | 13 | 0.25002 | 0.437 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 3.8125 | 1.125 | 6.5
SEISMIC | SST304 | 5 | AMSR-2E STANDARD | 091-01095-013 | 021-37035-001 | 391-01094-013 | 9 | 13 | 0.25002 | 0.437 | 0.75 | NO | YES | 3 | 1.125 | 4.875 | 6.5 | 3.125 | 9.875
SEISMIC | SST304 | 6 | AMSR-2E OFFSET | 091-01095-014 | 021-37035-001 | 391-01094-014 | 9 | 13 | 0.25002 | 0.437 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 4.5 | 1.125 | 7.875
SEISMIC | SST304 | 7 | AMSR-1C OFFSET SM | 091-01095-015 | 021-37034-001 | 391-01094-015 | 9 | 8.92 | 0.25002 | 0.437 | 0.5 | YES | NO | 4.5 | 3.75 | 5.25 | 3.8125 | 1.5625 | 6.0625
SEISMIC | SST304 | 8 | AMSR-2D OFFSET SM | 091-01095-016 | 021-37035-001 | 391-01094-016 | 9 | 8.92 | 0.25002 | 0.437 | 0.75 | YES | NO | 4.5 | 2.625 | 6.375 | 3.8125 | 1.125 | 6.5
Any changes to isolator plate, all-thread or plate assembly part numbers must also include updates to Isolator Part Select document in TKO Edit Manual document: Fans-025
Plate Assy Part Numbers can be found in Mapics and are connected to BOM_Map_30103_318 and BOM_Map_30103_143

## Isolators
Isolator Designation | VMC SPRING DESIGNATION | VMC FINAL SPRING SIZE | NOMINAL DEFLECTION, INCHES | JCI MINIMUM LOAD RANGE | JCI MAXIMUM LOAD RANGE | JCI SPRING P/N | OUTER SPRING COLOR | INNER SPRING COLOR | SPRING RATE, LB/IN | OPERATING HEIGHT, INCHES | Bolt Above Operating Height | Base Width | Base Length | Base Thickness | Base Hole Diameter | Base Hole Loc Width | Base Hole Loc Length | Housing Length | Tie Down Bolt Loc | Tie Down Bolt Diameter | Adjustment Bolt Diameter
ISO_D | [5 empty] | ISO_PN |  |  |  | ISO_OPHGT | ISO_BLT | ISO_BW | ISO_BL | ISO_BT | ISO_BHD | ISO_BHW | ISO_BHL | ISO_HL | ISO_TDBL | ISO_TDBD | ISO_ADJBD
1 | AMSR | 1c-50-Sb | 1 | 1 | 50 | 029 23800 115 | BLUE | NONE | 50 | 4.625 | 1 | 3 | 6 | 0.25 | 0.625 | 0.75 | 0.75 | 4.125 | 1.375 | 0.375 | 0.5
2 | AMSR | 1c-100-Sb | 1 | 51 | 100 | 029 23800 116 | TAN | NONE | 100 | 4.625 | 1 | 3 | 6 | 0.25 | 0.625 | 0.75 | 0.75 | 4.1253 | 1.375 | 0.375 | 0.5
3 | AMSR | 1c-150-Sb | 1 | 101 | 150 | 029 23800 117 | RED | NONE | 150 | 4.625 | 1 | 3 | 6 | 0.25 | 0.625 | 0.75 | 0.75 | 4.1253 | 1.375 | 0.375 | 0.5
4 | AMSR | 1c-250-Sb | 1 | 151 | 250 | 029 23800 118 | BLACK | NONE | 300 | 4.625 | 1 | 3 | 6 | 0.25 | 0.625 | 0.75 | 0.75 | 4.1253 | 1.375 | 0.375 | 0.5
5 | AMSR | 1c-300-Sb | 1 | 251 | 300 | 029 23800 119 | DK YELLOW | NONE | 400 | 4.625 | 1 | 3 | 6 | 0.25 | 0.625 | 0.75 | 0.75 | 4.1253 | 1.375 | 0.375 | 0.5
6 | AMSR | 1c-370-Sb | 1 | 301 | 370 | 029 23800 120 | YELLOW | NONE | 493 | 4.625 | 1 | 3 | 6 | 0.25 | 0.625 | 0.75 | 0.75 | 4.1253 | 1.375 | 0.375 | 0.5
7 | AMSR | 1c-520n-Sb | 1 | 371 | 520 | 029 23800 121 | YELLOW | GREEN | 693 | 4.625 | 1 | 3 | 6 | 0.25 | 0.625 | 0.75 | 0.75 | 4.1253 | 1.375 | 0.375 | 0.5
8 | AMSR | 2d-160-Sb | 2 | 0 | 160 | 029 23800 101 | YELLOW | NONE | 70 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
9 | AMSR | 2d-230-Sb | 2 | 161 | 230 | 029 23800 102 | GREEN | NONE | 100 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
10 | AMSR | 2d-355-Sb | 2 | 231 | 355 | 029 23800 110 | DK BROWN | NONE | 165 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
11 | AMSR | 2d-435-Sb | 2 | 356 | 435 | 029 23800 111 | RED | NONE | 230 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
12 | AMSR | 2d-600n-Sb | 2 | 436 | 600 | 029 23800 103 | RED | BLACK | 319 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
13 | AMSR | 2d-725-Sb | 2 | 601 | 725 | 029 23800 112 | TAN | NONE | 450 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
14 | AMSR | 2d-845-Sb | 2 | 726 | 845 | 029 23800 104 | PINK | NONE | 570 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
15 | AMSR | 2d-1000n-Sb | 2 | 846 | 1000 | 029 23800 105 | PINK | BLACK | 650 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
16 | AMSR | 2d-1320n-Sb | 2 | 1001 | 1320 | 029 23800 106 | PINK | GRAY | 927 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
17 | AMSR | 2d-1435n-Sb | 2 | 1321 | 1435 | 029 23800 107 | PINK | GRAY/ORANGE | 1002 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
18 | AMSR | 2d-1640n-Sb | 2 | 1436 | 1640 | 029 23800 108 | PINK | GRAY/DK BROWN | 1067 | 7.25 | 1.5 | 6 | 7.625 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
19 | AMSR | 2e-2050-Sb | 2 | 1641 | 2050 | 029 23800 109 | DK BLUE | NONE | 1250 | 8.125 | 1.063 | 6 | 9 | 0.375 | 0.875 | 1.125 | 1.125 | 6.44 | 2 | 0.5 | 0.625
This specific ID number is used in isolator Plate Designation calcs in Excel Calcs tab. If this number changes values in cells H11, H18, H23 & H30 must also change accordingly

## Iso Sup Angle
Isolator Designation | SPRING DESIGNATION | MAXIMUM LOAD | ISO SUPPORT ANGLE P/N | OPERATING HEIGHT | Angle Height | Angle Depth | Angle Length | Angle Thickness | Flange Thickness/ Radius | Hole Spacing | Hole Location | Hole Diameter 1 | Hole Diameter 2 | Weight
SUPANG_DESG |  |  | SUPANG_PN |  | SUPANG_H | SUPANG_D | SUPANG_L | SUPANG_WT | SUPANG_FTR | SUPANG_HS | SUPANG_HL | SUPANG_HD1 | SUPANG_HD2 | SUPANG_LB
1 | AMSR-1C T1 | 1300 | 091 20019 014 | 4.625 | 4 | 6 | 8 | 0.5 | 0.5 | 1.375 | 1.25 | 0.5 | 0.75 | 10.8
2 | AMSR-2D T1 | 1300 | 091 20019 010 | 7.25 | 4 | 6 | 8 | 0.5 | 0.5 | 2 | 1.25 | 0.625 | 0.875 | 10.8
3 | AMSR-2D T2 | 2500 | 091 20019 011 | 7.25 | 4 | 6 | 8 | 0.5 | 0.5 | 2 | 1.25 | 0.625 | 0.875 | 12.2
4 | AMSR-2E T1 | 1300 | 091 20019 012 | 8.125 | 4 | 6 | 8 | 0.5 | 0.5 | 2.5 | 1.25 | 0.625 | 0.875 | 10.8
5 | AMSR-2E T2 | 2500 | 091 20019 013 | 8.125 | 4 | 6 | 8 | 0.5 | 0.5 | 2.5 | 1.25 | 0.625 | 0.875 | 12.2
These specific values used in calcs in support angle offset calculations in Excel Calcs tab. If modified values in cells K103-K106 must be checked to verify desired output is maintained

## Hole Sizes
Standard Hole Sizes
Clearance |  |  | Engagement
1/8 Rivet | 0.152 |  | 1/8 Rivet | 0.140
3/16 Rivet | 0.218 |  | 3/16 Rivet | 0.208
#6 Hardware | 0.188 |  | 28-20 ga. (<.04 thickness)
#8 Hardware | 0.218 |  | #6 Hardware | 0.109
#10 Hardware | 0.218 |  | #8 Hardware | 0.109
1/4 Hardware | 0.312 |  | #10 Hardware | 0.109
5/16 Hardware | 0.375 |  | 1/4 Hardware - galv material | 0.109
3/8 Hardware | 0.437 |  | 1/4 Hardware - sst | 0.188 | Engagement holes per part
1/2 Hardware | 0.562 |  | 5/16 Hardware | 0.109 | InertiaPlateEngHole | 0.152
|  |  | 3/8 Hardware | 0.109
18-14 ga. (>=.04 and <=.09 thickness)
|  |  | #6 Hardware | 0.109
|  |  | #8 Hardware AB, B | 0.136
|  |  | #8 Hardware D,F,G &T | 0.140
|  |  | #10 Hardware | 0.152
|  |  | 1/4 Hardware AB, B | 0.188
|  |  | 1/4 Hardware D,F,G&T | 0.203
|  |  | 5/16 Hardware | 0.218
|  |  | 3/8 Hardware AB,B | 0.281
|  |  | 3/8 Hardware D,F,G&T | 0.312
12 ga and up (>.09 thickness)
|  |  | #8 Hardware | 0.152
|  |  | #10 Hardware | 0.152
|  |  | 1/4 Hardware AB, B | 0.203
|  |  | 1/4 Hardware D,F,G&T | 0.218
|  |  | 5/16 Hardware AB,B | 0.250
|  |  | 5/16 Hardware D,F,G&T | 0.281
|  |  | 3/8 Hardware AB,B | 0.312
|  |  | 3/8 Hardware D,F,G&T | 0.344
SPECIAL HOLE SIZES
Indicator holes
Ga | dia | spacing
28 ga - 14 ga (<=.09 thickness) | 0.125 | 0.125
12 ga - 10 ga (>.09 and < .14) | 0.188 | 0.188
8 ga. (>= .14 thickness) | 0.25 | 0.25
Standard hole sizes used in the project. Any special hole size needs to be listed below the special hole size heading. Hole sizes used in models should be referenced back to the hole size chart on this tab. Any changes to hole sizes must be done on the holes sizes tab.

## Material List
Page: 102-006 | [9 empty] | Edit Manual |  | PRODUCT: Solution
Title: Raw Material Part Numbers, Mapics Codes, Calculations And Others | [11 empty] | 102-006.xls |  |  |  | Rel/Rev Date:
[12 empty] | Revision Level : |  |  |  | ECN Number :
Solution Project, Raw material codes and calculations, Sheet or Coil stock, Square Foot
|  |  | Mat'l Group | Metal Gauge | Metal Thickness Min. | Design Thickness (Ref) | Inventor Thickness Key_PK | Active Product "XT" | Active Product "YC" | Mapics Part Number | Material description | Material Type | York "R" Std | Max Cut Size | Unit of Measure | Inventor Material Designation | "DXF" Mat'l Data | Hole Size / Texture | Staggered Centers
MAT_LOOKUP |  |  | MAT_GRP | MAT_GA | MAT_MINT | MAT_DEST | MAT_KEYT | MAT_XT | MAT_YC | MAT_PNUM | MAT_DESC | MAT_TYPE | MAT_RSTD | MAT_CUT | MAT_UMSR | MAT_DESG | MAT_DXF | MAT_HLSZ | MAT_STG
Sheet Products, Solid
3STL GALV |  |  | Sheet, G90 | 3 | 0.25 | 0.25 | 0.25001 |  | YC | 005 06145 003 | Galvanized Steel | G90 | R259 w/ note 4 | 60 X 144 | SF | STL GALV | GLVS250- | N/A | N/A
8STL GALV |  |  | Sheet, G90 | 8 | .156 | .156 | 0.15601 | XT | YC | 005 06145 008 | Galvanized Steel | G90 | R259 w/ note 4 | 48 X 144 | SF | STL GALV | GLVS157- | N/A | N/A
10STL GALV |  |  | Sheet, G90 | 10 | .125 | .126 | 0.12601 | - | YC | 005 06145 010 | Galvanized Steel | G90 | R259 w/ note 4 | 48 X 144 | SF | STL GALV | GLVS126- | N/A | N/A
12STL GALV |  |  | Sheet, G90 | 12 | .096 | .097 | 0.09701 | - | YC | 005 06145 012 | Galvanized Steel | G90 | R259 w/ note 4 | 60 X 144 | SF | STL GALV | GLVS097- | N/A | N/A
14STL GALV |  |  | Sheet, G90 | 14 | .069 | .070 | 0.07001 | - | YC | 005 06145 014 | Galvanized Steel | G90 | R259 w/ note 4 | 60 X 144 | SF | STL GALV | GLVS070- | N/A | N/A
16STL GALV |  |  | Sheet, G90 | 16 | .055 | .056 | 0.05601 | XT | YC | 005 06145 016 | Galvanized Steel | G90 | R259 w/ note 4 | 60 X 144 | SF | STL GALV | GLVS056A | N/A | N/A
18STL GALV |  |  | Sheet, G90 | 18 | .044 | .045 | 0.04501 | XT | YC | 005 06145 018 | Galvanized Steel | G90 | R259 w/ note 4 | 60 X 144 | SF | STL GALV | GLVS045A | N/A | N/A
20STL GALV |  |  | Sheet, G90 | 20 | .033 | .034 | 0.03401 | XT | YC | 005 06145 020 | Galvanized Steel | G90 | R259 w/ note 4 | 60 X 144 | SF | STL GALV | GLVS034- | N/A | N/A
22STL GALV |  |  | Sheet, G90 | 22 | .028 | .028 | 0.02801 | - | YC | 005 06145 022 | Galvanized Steel | G90 | R259 w/ note 4 | 60 X 144 | SF | STL GALV | GLVS028- | N/A | N/A
24STL GALV |  |  | Sheet, G90 | 24 | .022 | .022 | 0.02201 | XT | YC | 005 06145 024 | Galvanized Steel | G90 | R259 w/ note 4 | 60 X 144 | SF | STL GALV | GLVS022- | N/A | N/A
16STL GALV2 |  |  | Roll Form Coil | 16 | .055 | .056 | 0.05605 | - | YC | 001 07591 467 | Channel,Rf,16ga,Glv,4.67w_Flat, YC 2" Housing Channel | G40 | R259 w/ note 4 | 4.67 X Lg | SF | STL GALV2 | GLVS056C | N/A | N/A
16STL GALV3 |  |  | Roll Form Coil | 16 | .055 | .056 | 0.05606 | - | YC | 001 07591 567 | Channel,Rf,16ga,Glv,5.67w_Flat, YC 3" Housing Channel | G40 | R259 w/ note 4 | 5.67 X Lg | SF | STL GALV3 | GLVS056D | N/A | N/A
16STL GALV4 |  |  | Roll Form Coil | 16 | .055 | .056 | 0.05607 | - | YC | 001 07591 667 | Channel,Rf,16ga,Glv,6.67w_Flat, YC 4" Housing Channel | G40 | R259 w/ note 4 | 6.67 X Lg | SF | STL GALV4 | GLVS056E | N/A | N/A
18STL GALVS |  |  | Roll Form Coil | 18 | .044 | .045 | 0.04502 | XT | - | 005 06160 001 | Galvanized Steel, Coil, XT Seam Cap | G90 | R259 w/ note 4 | 2.491 X Lg | SF | STL GALVS | GLVS045B | N/A | N/A
16STL GALVR |  |  | Roll Form Coil | 16 | .055 | .056 | 0.05602 | XT | - | 005 06161 001 | Galvanized Steel, Coil, XT Raceway | G90 | R259 w/ note 4 | 12.62 X Lg | SF | STL GALVR | GLVS056B | N/A | N/A
14STL GALV PPG |  |  | Sheet, Pre-Paint | 14 | .069 | .070 | 0.07003 | - | YC | 005 07110 014 | Sheet,Pre-Paint,Gray,14ga | P-Paint | M-310 | 48 x Lg | SF | STL GALV PPG | GLVPP070A | Gray Paint | N/A
16STL GALV PPG |  |  | Sheet, Pre-Paint | 16 | .055 | .056 | 0.05603 | - | YC | 005 07110 016 | Sheet,Pre-Paint,Gray,16ga | P-Paint | M-310 | 48 x Lg | SF | STL GALV PPG | GLVPP056A | Gray Paint | N/A
16STL GALV PPC |  |  | Sheet, Pre-Paint | 16 | .055 | .056 | 0.05604 | - | YC | 005 07110 116 | Sheet,Pre-Paint,Champagne,16ga | P-Paint | M-310 | 48 x Lg | SF | STL GALV PPC | GLVPP056B | Champagne Paint | N/A
18STL GALV PPW |  |  | Sheet, Pre-Paint | 18 | .044 | .045 | 0.04503 | - | YC | 005 07110 117 | Sheet,Pre-Paint,Msftwhite,18ga | P-Paint | M-310 | 48 x Lg | SF | STL GALV PPW | GLVPP045A | Msftwhite Paint | N/A
18STL GALV PPC |  |  | Sheet, Pre-Paint | 18 | .044 | .045 | 0.04504 | - | YC | 005 07110 118 | Sheet,Pre-Paint,Champagne,18ga | P-Paint | M-310 | 48 x Lg | SF | STL GALV PPC | GLVPP045B | Champagne Paint | N/A
10STL HOT ROLL |  |  | Sheet, HR | 10 | .127 | .127 | 0.12701 | - | YC | 005 07113 010 | Sheet,Hot-Rolled,10ga | HR | - | 48 X 144 | SF | STL HOT ROLL | STLHR127A | Hot-Rolled | N/A
11STL HOT ROLL |  |  | Sheet, HR | 11 | .112 | .112 | 0.11201 | - | YC | 005 07113 011 | Sheet,Hot-Rolled,11ga | HR | - | 48 X 96 | SF | STL HOT ROLL | STLHR112A | Hot-Rolled | N/A
12STL HOT ROLL |  |  | Sheet, HR | 12 | .097 | .097 | 0.09704 | - | YC | 005 07113 012 | Sheet,Hot-Rolled,12ga | HR | - | 48 X 96 | SF | STL HOT ROLL | STLHR097A | Hot-Rolled | N/A
14STL HOT ROLL |  |  | Sheet, HR | 14 | .068 | .068 | 0.06801 | - | YC | 005 07113 014 | Sheet,Hot-Rolled,14ga | HR | - | 48 X 120 | SF | STL HOT ROLL | STLHR068A | Hot-Rolled | N/A
20ALM SHT |  |  | Sheet, AL | 20 | .040 | .040 | 0.04001 | - | YC | 008 02570 040 | Sheet,Al,3003h14,.040 | AL | R-777 | 48 x 144 | SF | ALM SHT | ALUS040A | N/A | N/A
18ALM SHT |  |  | Sheet, AL | 18 | .050 | .050 | 0.05003 | - | YC | 008 02570 050 | Sheet,Al,3003h14,.050 | AL | R-777 | 48 x 144 | SF | ALM SHT | ALUS050A | N/A | N/A
16ALM SHT |  |  | Sheet, AL | 16 | .063 | .063 | 0.06301 | - | YC | 008 02570 063 | Sheet,Al,3003h14,.063 | AL | R-777 | 48 x 144 | SF | ALM SHT | ALUS063A | N/A | N/A
14ALM SHT |  |  | Sheet, AL | 14 | .080 | .080 | 0.08001 | - | YC | 008 02570 080 | Sheet,Al,3003h14,.080 | AL | R-777 | 48 x 144 | SF | ALM SHT | ALUS080A | N/A | N/A
10ALM SHT |  |  | Sheet, AL | 10 | .125 | .125 | 0.12501 | - | YC | 008 02570 125 | Sheet,Al,3003h14,.125 | AL | R-777 | 48 x 144 | SF | ALM SHT | ALUS125A | N/A | N/A
8ALM SHT |  |  | Sheet, AL | 8 | .190 | .190 | 0.19001 | - | YC | 008 02570 190 | Sheet,Al,3003h14,.190 | AL | R-777 | 48 x 144 | SF | ALM SHT | ALUS190A | N/A | N/A
8SST304 |  |  | Sheet, SST | 8 | .165 | .165 | 0.16501 | N/A | N/A | 005 06146 008 | Stainless steel | 304 | R52 | 48 X 144 | SF | SST304 | SSTS165- | N/A | N/A
10SST304 |  |  | Sheet, SST | 10 | .135 | .135 | 0.13501 | XT | YC | 005 06146 010 | Stainless steel | 304 | R52 | 48 X 144 | SF | SST304 | SSTS135- | N/A | N/A
12SST304 |  |  | Sheet, SST | 12 | .105 | .105 | 0.10501 | XT | YC | 005 06146 012 | Stainless steel | 304 | R52 | 60 X 144 | SF | SST304 | SSTS105- | N/A | N/A
14SST304 |  |  | Sheet, SST | 14 | .075 | .075 | 0.07501 | XT | YC | 005 06146 014 | Stainless steel | 304 | R52 | 60 X 144 | SF | SST304 | SSTS075- | N/A | N/A
16SST304 |  |  | Sheet, SST | 16 | .060 | .060 | 0.06001 | XT | YC | 005 06146 016 | Stainless steel | 304 | R52 | 60 X 144 | SF | SST304 | SSTS060- | N/A | N/A
18SST304 |  |  | Sheet, SST | 18 | .048 | .048 | 0.04801 | XT | YC | 005 06146 018 | Stainless steel | 304 | R52 | 60 X 144 | SF | SST304 | SSTS048- | N/A | N/A
20SST304 |  |  | Sheet, SST | 20 | .035 | .035 | 0.03501 | XT | YC | 005 06146 020 | Stainless steel | 304 | R52 | 60 X 144 | SF | SST304 | SSTS035- | N/A | N/A
22SST304 |  |  | Sheet, SST | 22 | .029 | .029 | 0.02901 | - | YC | 005 06146 022 | Stainless steel | 304 | R52 | 60 X 144 | SF | SST304 | SSTS029- | N/A | N/A
24SST304 |  |  | Sheet, SST | 24 | .024 | .024 | 0.02401 | N/A | N/A | 005 06146 024 | Stainless steel | 304 | R52 | 60 X 144 | SF | SST304 | SSTS024- | N/A | N/A
12SST304L |  |  | Sheet, SST | 12 | .105 | .105 | 0.10502 | - | YC | 005 07103 012 | Sheet,304lss,12ga | 304L | R52 | 60 X 144 | SF | SST304L | SSTL105- | N/A | N/A
16SST304L |  |  | Sheet, SST | 16 | .060 | .060 | 0.06002 | - | YC | 005 07103 016 | Sheet,304lss,16ga | 304L | R52 | 60 X 144 | SF | SST304L | SSTL060- | N/A | N/A
10SST316L |  |  | Sheet, SST | 10 | .135 | .135 | 0.13502 | - | YC | 005 07104 010 | Sheet,316lss, 10ga | 316L | R52 | 60 X 144 | SF | SST316L | SSLS135- | N/A | N/A
12SST316L |  |  | Sheet, SST | 12 | .105 | .105 | 0.10503 | - | YC | 005 07104 012 | Sheet,316lss, 12ga | 316L | R52 | 60 X 144 | SF | SST316L | SSLS105- | N/A | N/A
14SST316L |  |  | Sheet, SST | 14 | .075 | .075 | 0.07502 | - | YC | 005 07104 014 | Sheet,316lss, 14ga | 316L | R52 | 60 X 144 | SF | SST316L | SSLS075- | N/A | N/A
16SST316L |  |  | Sheet, SST | 16 | .060 | .060 | 0.06003 | XT | YC | 005 07104 016 | Sheet,316lss, 16ga | 316L | R52 | 60 X 144 | SF | SST316L | SSLS060- | N/A | N/A
18SST316L |  |  | Sheet, SST | 18 | .048 | .048 | 0.04802 | XT | YC | 005 07104 018 | Sheet,316lss, 18ga | 316L | R52 | 60 X 144 | SF | SST316L | SSLS048- | N/A | N/A
20SST316L |  |  | Sheet, SST | 20 | .035 | .035 | 0.03502 | XT | YC | 005 07104 020 | Sheet,316lss, 20ga | 316L | R52 | 60 X 144 | SF | SST316L | SSLS035- | N/A | N/A
22SST316L |  |  | Sheet, SST | 22 | .029 | .029 | 0.02902 | - | YC | 005 07104 022 | Sheet,316lss, 22ga | 316L | R52 | 60 X 144 | SF | SST316L | SSLS029- | N/A | N/A
Sheet Products, Structural
10STRUCT GALV |  |  | Sheet, Structural | 10 | .125 | .126 | 0.12602 | XT | - | 005 06596 010 | Structural Galvanized Steel | G90 | R1190 | 48 X 144 | SF | STRUCT GALV | GLVS126S | N/A | N/A
12STRUCT GALV |  |  | Sheet, Structural | 12 | .096 | .097 | 0.09702 | XT | - | 005 06596 012 | Structural Galvanized Steel | G90 | R1190 | 60 X 144 | SF | STRUCT GALV | GLVS097S | N/A | N/A
14STRUCT GALV |  |  | Sheet, Structural | 14 | .069 | .070 | 0.07002 | XT | - | 005 06596 014 | Structural Galvanized Steel | G90 | R1190 | 60 X 144 | SF | STRUCT GALV | GLVS070S | N/A | N/A
Sheet Products, Perforated
20GALV PRFA |  |  | Sheet, Perf | 20 | .039 | .039 | 0.03901 | XT | - | 005 02897 000 | Galvanized Steel (perf) | G90 | R1045 | 48 X 120 | SF | GALV PRFA | GLVP039A | 5/16 | 3/8
20GALV PRFD |  |  | Sheet, Perf | 20 | .039 | .039 | 0.03902 | XT | - | 005 02901 000 | Galvanized Steel (perf) | G90 | R1045 | 48 X 120 | SF | GALV PRFD | GLVP039D | 1/4 | 3/8
20GALV PRFE |  |  | Sheet, Perf | 20 | .039 | .039 | 0.03903 | XT | - | 005 06154 000 | Galvanized Steel (perf) | G90 | R1045 | 48 X 120 | SF | GALV PRFE | GLVP039E | 5/8 | 13/16
16GALV PRFG |  |  | Sheet, Perf | 16 | .055 | .055 | 0.05501 | - | YC | 005 07115 016 | Sheet,Perf,Glv,40.3%,16ga | G90 | R1045 | 48 X Lg | SF | GALV PRFG | GLVP055A | .125 | .188
18GALV PRFG |  |  | Sheet, Perf | 18 | .044 | .044 | 0.04505 | - | YC | 005 07115 018 | Sheet,Perf,Glv,40.3%,18ga | G90 | R1045 | 48 X 120 | SF | GALV PRFG | GLVP045A | .125 | .188
20GALV PRFG |  |  | Sheet, Perf | 20 | .033 | .034 | 0.03402 | - | YC | 005 07115 020 | Sheet,Perf,Glv,40.3%,20ga | G90 | R1045 | 48 X 144 | SF | GALV PRFG | GLVP034A | .125 | .188
22GALV PRFF |  |  | Sheet, Perf | 22 | .028 | .028 | 0.02802 | XT | YC | 005 07115 022 | Sheet,Perf,Glv,40.3%,22ga | G90 | R1045 | 60 X 144 | SF | GALV PRFF | GLVP028A | .125 | .188
18GALV PRFH |  |  | Sheet, Perf | 18 | .044 | .044 | 0.044 | - | YC | 005 07118 018 | Sheet,Perf,Glv,47%,18ga | G90 | R1045 | 48 X 120 | SF | GALV PRFH | GLVP044B | .50 | .688
18ALM PRF |  |  | Sheet, Perf, AL | 18 | .050 | .050 | 0.05001 | XT | - | 008 02316 001 | Aluminum Sheet (perf) | AL | R1116 | 60 X 144 | SF | ALM PRF | ALUP050A | 1/8 | 7/32
18ALM PRFA |  |  | Sheet, Perf, AL | 18 | .050 | .050 | 0.05002 | - | YC | 008 02573 050 | Sheet,Perf,Al,40.3%,.050, 3003h14 | AL | - | 48 x 144 | SF | ALM PRFA | ALUP050B | .125 | .188
16ALM PRFA |  |  | Sheet, Perf, AL | 16 | .063 | .063 | 0.06302 | - | YC | 008 02573 063 | Sheet,Perf,Al,40.3%,.063, 3003h14 | AL | - | 48 x 144 | SF | ALM PRFA | ALUP063A | .125 | .188
14ALM PRFA |  |  | Sheet, Perf, AL | 14 | .080 | .080 | 0.08003 | - | YC | 008 02573 080 | Sheet,Perf,Al,40.3%,.080, 3003h14 | AL | - | 48 x 144 | SF | ALM PRFA | ALUP080A | .125 | .188
14ALM PRFB |  |  | Sheet, Perf, AL | 14 | .080 | .080 | 0.08004 | - | YC | 008 02574 080 | Sheet,Perf,Al,47%,.080, 3003h14 | AL | - | 48 x 144 | SF | ALM PRFB | ALUP080B | .50 | .688
16SST304PA |  |  | Sheet, Perf, SST | 16 | .060 | .060 | 0.06004 | - | YC | 005 07114 016 | Sheet,Perf,304ss,40.3%,16ga | 304 | R52 | 60 X 144 | SF | SST304PA | SSTP060A | .125 | .188
18SST304PA |  |  | Sheet, Perf, SST | 18 | .048 | .048 | 0.04803 | - | YC | 005 07114 018 | Sheet,Perf,304ss,40.3%,18ga | 304 | R52 | 60 X 144 | SF | SST304PA | SSTP048B | .125 | .188
20SST304PA |  |  | Sheet, Perf, SST | 20 | .035 | .035 | 0.03503 | - | YC | 005 07114 020 | Sheet,Perf,304ss,40.3%,20ga | 304 | R52 | 60 X 144 | SF | SST304PA | SSTP035A | .125 | .188
16SST304PC |  |  | Sheet, Perf, SST | 16 | .060 | .060 | 0.06005 | - | YC | 005 07116 016 | Sheet,Perf,304ss,51%,16ga | 304 | R52 | 60 X 144 | SF | SST304PC | SSTP060B | .188 | .25
18SST304PB |  |  | Sheet, Perf, SST | 18 | .048 | .048 | 0.04804 | - | YC | 005 07117 018 | Sheet,Perf,304ss,47%,18ga | 304 | R52 | 60 X 144 | SF | SST304PB | SSTP048C | .50 | .688
Sheet Products, Expanded or Textured
9GALV EXPA |  |  | Sheet, Expanded | 9 | .146 | .146 | 0.14602 | XT | - | 005 06150 000 | Galvanized Steel (Expanded/Flattened) 3/4 No. 9 | G90 | R259 | 48 x 120 | SF | GALV EXPA | GLVE146A | 3/4" wide diamond | Flattened
9GALV EXPB |  |  | Sheet, Expanded | 9 | .146 | .146 | 0.14601 | XT | - | 005 06579 000 | Galvanized Steel (Expanded/Flattened) 1-1/2 No. 9 | G90 | R259 | 48 x 120 | SF | GALV EXPB | GLVE146B | 1-1/2" wide diamond | Flattened
9GALV EXPBY |  |  | Sheet, Expanded | 9 | .146 | .146 | 0.14604 | - | YC | 005 06579 100 | Sheet,Exp_Mtl,Glv,G90,9ga, 1.5 Flattened | G90 | R259 | 48 x 96 | SF | GALV EXPBY | GLVE146C | 1-1/2" wide diamond | Flattened
11GALV EXPA |  |  | Sheet, Expanded | 11 | .120 | .120 | 0.12001 | - | YC | 005 07109 011 | Sheet,Exp_Mtl,Glv,11ga, .75 Flattened, #9 | G90 | R259 | 48 x 120 | SF | GALV EXPA | GLVE120- | 3/4" wide diamond | Flattened
16ALM EXP |  |  | Sheet, Expanded, AL | 16 | .060 | .060 | 0.06006 | XT | - | 008 02335 000 | Aluminum Sht (Expanded/Flattened) 1/2 No..081 5005-H34 | AL | - | 48 X 120 | SF | ALM EXP | ALUE060A | .28x.94 diamond | Flattened
9SST304E |  |  | Sheet, Expanded, SST | 9 | .146 | .146 | 0.14603 | - | YC | 005 06588 100 | Sheet,Exp_Mtl,Ss,304,9ga,1.5 Flattened | 304 | R52 | 48 x 96 | SF | SST304E | SSTE146- | 1-1/2" wide diamond | Flattened
11SST304E |  |  | Sheet, Expanded, SST | 11 | .120 | .120 | 0.12002 | - | YC | 005 07120 011 | Sheet,Exp_Mtl,304ss,11ga, .75 flattened #9 | 304 | R52 | 60 X 144 | SF | SST304E | SSTE120- | 3/4" wide diamond | Flattened
20ALM EMB |  |  | Sheet, AL, Emb | 20 | .040 | .040 | 0.04002 | - | YC | 008 02168 000 | Al,3105h14,.040, Stucco Emb Alum | AL | Stucco Finish | 48 x 144 | SF | ALM EMB | ALUE040A | Embossed AL | N/A
14ALM EMB |  |  | Sheet, AL, Emb | 14 | .080 | .080 | 0.08002 | - | YC | 008 02571 080 | Sheet,Al_Text,3003h134,.080_Stucco | AL | Stucco Finish | 48 x 144 | SF | ALM EMB | ALUE080A | Embossed AL | N/A
1SST304G |  |  | Grating | 1 | 1"High | 1"High | 1 | - | YC | 001 07514 000 | Grating,19-S-4,1h_.13thk ,Stainless Steel Grating | 304 | R52 | 36 X 96 | SF | SST304G | SSTG100A | 1" 19-S-4 | N/A
1ALM GRATE |  |  | Grating | 1 | 1"High | 1"High | 1 | - | YC | 001 07515 000 | Grating,19-Ap-4,1h_.13thk,Aluminum Grating | AL | - | 36 X 96 | SF | ALM GRATE | ALUG100A | 1" 19-Ap-4 | N/A
1GALV GRATE |  |  | Grating | 1 | 1"High | 1"High | 1 | - | YC | 001 07516 000 | Grating,19-W-4,1h_.13thk ,Hot Dipped Glv Grating | G90 | Hot Dip | 36 X 96 | SF | GALV GRATE | GLVG100A | 1" 19-W-4 | N/A
19GALV CLOTH |  |  | Sheet, Cloth | 19 | .04 | .04 | 0.04003 | - | YC | 005 07112 041 | Cloth, Hdw, Glv, .5 x .5 x .04 | G90 | Galv | 48 x 120 | SF | GALV CLOTH | GLVC040A | N/A | N/A
Sheet Products, Diamond Tread Plate
12STL DIA HR |  |  | Plate, Diamond, HR | 12 | .096 | .097 | 0.09703 | - | YC | 005 07108 012 | Plate,Dia,Hot-Rolled,12ga | HR | - | 48 X 96 | SF | STL DIA HR | HRSD097- | Raised Lug | N/A
14STL DIA HR |  |  | Plate, Diamond, HR | 14 | .069 | .070 | 0.07004 | - | YC | 005 07108 014 | Plate,Dia,Hot-Rolled,14ga | HR | - | 48 X 120 | SF | STL DIA HR | HRSD070- | Raised Lug | N/A
10STL DIA HR |  |  | Plate, Diamond, HR | 10 | .125 | .126 | 0.12603 | - | YC | 005 07108 125 | Plate,Dia,Hot-Rolled,.125 | HR | - | 48 X 144 | SF | STL DIA HR | HRSD126- | Raised Lug | N/A
7STL DIA HR |  |  | Plate, Diamond, HR | 7 | .188 | .188 | 0.18801 | - | YC | 005 07108 188 | Plate,Dia,Hot-Rolled,.188 | HR | - | 48 X 120 | SF | STL DIA HR | HRSD188- | Raised Lug | N/A
11ALM DIA |  |  | Plate, Diamond, AL | 11 | .100 | .100 | 0.10001 | - | YC | 008 02572 100 | Plate,Dia,Al,.100_3003 | AL | - | 48 x 144 | SF | ALM DIA | ALUD100A | Raised Lug | N/A
1/8ALM DIA |  |  | Plate, Diamond, AL | 1/8 | .125 | .125 | 0.12503 | XT | YC | 008 02572 125 | Plate,Dia,Al,.125_3003 | AL | - | 60 X 144 | SF | ALM DIA | ALUD125A | Raised Lug | N/A
3/16ALM DIA |  |  | Plate, Diamond, AL | 3/16 | .188 | .188 | 0.18802 | - | YC | 008 02572 188 | Plate,Dia,Al,.188_3003 | AL | - | 48 x 144 | SF | ALM DIA | ALUD188A | Raised Lug | N/A
1/8ALMB DIA |  |  | Plate, Diamond, AL | 1/8 | .125 | .125 | 0.12504 | - | YC | 008 02596 101 | Plate,Dia,Alu,.125_3003 Bright | AL | - | 48 x 144 | SF | ALMB DIA | ALUD125B | Raised Lug | N/A
3/16ALMB DIA |  |  | Plate, Diamond, AL | 3/16 | .188 | .188 | 0.18804 | - | YC | 008 02596 102 | Plate,Dia,Alu,.188_3003 Bright | AL | - | 48 x 144 | SF | ALMB DIA | ALUD188B | Raised Lug | N/A
1/4ALMB DIA |  |  | Plate, Diamond, AL | 1/4 | .250 | .250 | 0.25003 | - | YC | 008 02596 103 | Plate,Dia,Alu,.25_3003 Bright | AL | - | 48 x 144 | SF | ALMB DIA | ALUD250B | Raised Lug | N/A
1/8SST304D |  |  | Plate, Diamond, SST | 1/8 | .125 | .125 | 0.12502 | - | YC | 005 07107 125 | Plate,Dia,304ss,.125 | 304 | R52 | 48 X 120 | SF | SST304D | SSTD125- | Raised Lug | N/A
3/16SST304D |  |  | Plate, Diamond, SST | 3/16 | .188 | .188 | 0.18805 | - | YC | 005 07107 188 | Plate,Dia,304ss,.188 | 304 | R52 | 48 X 120 | SF | SST304D | SSTD188- | Raised Lug | N/A
Sheet Products, Corrugated
20GALV CORA |  |  | Sheet, Corrugated | 20 | .034 | .034 | 0.03403 | XT | - | 005 06169 010 | Galvanized Steel, Corrugated, 4” Box Rib Profile | G90 | - | 38.5 X 120 | SF | GALV CORA | GLVC034A | Corrugated | N/A
Plate Products, Solid
7SST304 |  |  | Plate, SST | 7 | .188 | .188 | 0.18803 | - | YC | 005 06146 188 | Plate,304ss,.188 | 304 | R52 | 60 X 144 | SF | SST304 | SSTS188- | N/A | N/A
3SST304 |  |  | Plate, SST | 3 | .250 | .250 | 0.25002 | - | YC | 005 06146 250 | Plate,304ss,.25 | 304 | R52 | 60 X 144 | SF | SST304 | SSTS250- | N/A | N/A
7STL PLATE |  |  | Plate, Steel | 7 | .188 | .188 | 0.18806 | - | YC | 005 07119 188 | Plate,Steel 0.188 | Mild | - | 48 x 120 | SF | STL PLATE | STLPL188A | N/A | N/A
3STL PLATE |  |  | Plate, Steel | 3 | .250 | .250 | 0.25001 | - | YC | 005 07119 250 | Plate,Steel,0.25 | Mild | - | 48 x 120 | SF | STL PLATE | STLPL250A | N/A | N/A
0STL PLATE |  |  | Plate, Steel | 0 | .313 | .313 | 0.31301 | - | YC | 005 07119 313 | Plate,Steel,0.313 | Mild | - | 48 x 120 | SF | STL PLATE | STLPL313A | N/A | N/A
000STL PLATE |  |  | Plate, Steel | 000 | .375 | .375 | 0.37501 | - | YC | 005 07119 375 | Plate,Steel,0.375 | Mild | - | 48 x 120 | SF | STL PLATE | STLPL375A | N/A | N/A
0000000STL PLATE |  |  | Plate, Steel | 0000000 | .500 | .500 | 0.5 | - | YC | 005 07119 500 | Plate,Steel,0.5 | Mild | - | 48 x 120 | SF | STL PLATE | STLPL500A | N/A | N/A
Notes:
1. All sheet or coil stock raw material will be calculated in Square Foot, (Width" X Length") / 144 = SQ. FT.
2. Conversions to Pounds or Sheets will be setup in Mapics as a (1 to X) product structure relationship
3. The max sheet size is 60 X 144 inches for sheet stock material
4. With the exception to standard R259 is that all Galvanized Steel will be Chemically Treated and oiled with a mineral based oil which is easily removable by vapor degreasing or mild alkaline cleaning with a hot water rinse.

## Steel List
Solution Project, Raw material codes and calculations, Sheet or Coil stock, Square Foot
|  |  | Mat'l Group | LBS/FT | Web/Wall Thickness | Height | Depth | Flange Thickness/ Radius | Active Product "XT" | Active Product "YC" | Mapics Part Number | Material description | Material Type | York "R" Std | Max Cut Size | Unit of Measure | Inventor Material Designation | "DXF" Mat'l Data
STL_LOOKUP |  |  | STL_GRP | STL_LBFT | STL_WT | STL_H | STL_D | STL_FTR | STL_XT | STL_YC | STL_PNUM | STL_DESC | STL_TYPE | STL_RSTD | STL_CUT | STL_UMSR | STL_DESG | STL_DXF
Structural Steel, Shapes
Channel20.56 |  |  | Steel, Channel | 0.56 | 0.188 | 2 | 1.000 | 0.188 | - | YC | 001-07500-000 | Channel 2 X 1 X .19,R-18 Std | A572 HRS | R18 | 324 IN length | IN | - | -
Channel34.1 |  |  | Steel, Channel | 4.1 | 0.17 | 3 | 1.41 | 0.273 | - | YC | 001-07501-000 | Channel 3 X 4.1 Lb/Ft,R-18 Std | A572 HRS | R18 | 324 IN length | IN | - | -
Channel35 |  |  | Steel, Channel | 5 | 0.258 | 3 | 1.498 | 0.273 | XT | - | 001 08405 003 | 3" x 5.0# Structural Channel | A572 HRS | R18 | 324 IN length | IN | - | -
Channel45.4 |  |  | Steel, Channel | 5.4 | 0.184 | 4 | 1.584 | 0.296 | XT | YC | 001 08405 004 | 4" x 5.4# Structural Channel | A572 HRS | R18 | 324 IN length | IN | - | -
Channel47.25 |  |  | Steel, Channel | 7.25 | 0.321 | 4 | 1.721 | 0.296 | XT | - | 001 08405 104 | 4" x 7.25# Structural Channel | A572 HRS | R18 | 324 IN length | IN | - | -
Channel56.7 |  |  | Steel, Channel | 6.7 | 0.19 | 5 | 1.75 | 0.32 | - | YC | 001 08405 005 | Channel 5 X 6.7 Lb/Ft,R-18 Std | A572 HRS | R18 | 324 IN length | IN | - | -
Channel68.2 |  |  | Steel, Channel | 8.2 | 0.2 | 6 | 1.92 | 0.343 | XT | YC | 001 08405 006 | 6" x 8.2# Structural Channel | A572 HRS | R18 | 324 IN length | IN | - | -
Channel811.5 |  |  | Steel, Channel | 11.5 | 0.22 | 8 | 2.26 | 0.39 | XT | YC | 001 08405 008 | 8" x 11.5# Structural Channel | A572 HRS | R18 | 324 IN length | IN | - | -
Channel1015.3 |  |  | Steel, Channel | 15.3 | 0.24 | 10 | 2.6 | 0.438 | XT | YC | 001 08405 010 | 10" x 15.3# Structural Channel | A572 HRS | R18 | 324 IN length | IN | - | -
Channel1220.7 |  |  | Steel, Channel | 20.7 | 0.282 | 12 | 2.942 | 0.501 | XT | YC | 001 08405 012 | 12" x 20.7# Structural Channel | A572 HRS | R18 | 324 IN length | IN | - | -
I-Beam35.7 |  |  | Steel, I-Beam | 5.7 | 0.17 | 3 | 2.33 | 0.26 | - | YC | 001-07638-000 | I-Beam 3 X 5.7 Lb/Ft, R-18 Std | A36 HRS | R18 | 324 IN length | IN | - | -
I-Beam47.7 |  |  | Steel, I-Beam | 7.7 | 0.19 | 4 | 2.66 | 0.293 | XT | YC | 001-08409-004 | I-Beam 4 X 7.7 Lb/Ft,R-18 Std | A36 HRS | R18 | 324 IN length | IN | - | -
I-Beam612.5 |  |  | Steel, I-Beam | 12.5 | 0.23 | 6 | 3.33 | 0.359 | - | YC | 001-07509-000 | I-Beam 6 X 12.5 Lb/Ft,R-18 Std | A36 HRS | R18 | 324 IN length | IN | - | -
I-Beam818.4 |  |  | Steel, I-Beam | 18.4 | 0.27 | 8 | 4 | 0.425 | - | YC | 001-07510-000 | I-Beam 8 X 18.4 Lb/Ft,R-18 Std | A36 HRS | R18 | 324 IN length | IN | - | -
Angle0.750.750.125 |  |  | Steel, Angle | 0.59 | 0.125 | 0.75 | 0.75 | 0.125 | XT | - | 001 08406 075 | 3/4" x 3/4" x 1/8" Structural Angle | A36 HRS | R18 | 324 IN length | IN | - | -
Angle110.25 |  |  | Steel, Angle | 1.49 | 0.25 | 1 | 1 | 0.125 | XT | - | 001 08406 100 | 1" x 1" x 1/4" Structural Angle | A36 HRS | R18 | 324 IN length | IN | - | -
Angle1.251.250.25 |  |  | Steel, Angle | 1.92 | 0.25 | 1.25 | 1.25 | 0.188 | XT | - | 001 08406 125 | 1-1/4" x 1-1/4" x 1/4" Structural Angle | A36 HRS | R18 | 324 IN length | IN | - | -
Angle1.51.50.25 |  |  | Steel, Angle | 2.34 | 0.25 | 1.5 | 1.5 | 0.188 | XT | - | 001 08406 150 | 1-1/2" x 1-1/2" x 1/4" Structural Angle | A36 HRS | R18 | 324 IN length | IN | - | -
Angle220.25 |  |  | Steel, Angle | 3.19 | 0.25 | 2 | 2 | 0.281 | XT | YC | 001 08406 200 | 2" x 2" x 1/4" Structural Angle | A36 HRS | R18 | 324 IN length | IN | - | -
AngleCoped220.25 |  |  | Steel, AngleCoped | 3.19 | 0.25 | 2 | 2 | 0.281 | XT | - | 001 08407 200 | 2" x 2" x 1/4" Structural Angle, Coped Both Ends | A36 HRS | R18 | 324 IN length | IN | - | -
Angle220.188 |  |  | Steel, Angle | 2.44 | 0.188 | 2 | 2 | 0.281 | - | YC | 001-05057-000 | Angle Blk 2 X 2 X .19 | A36 HRS | R18 | 324 IN length | IN | - | -
Angle430.375 |  |  | Steel, Angle | 8.5 | 0.375 | 4 | 3 | 0.5 | - | YC | 001 08406 403 | Angle Blk 4 x 3 x .38 thk | A36 HRS | R19 | 324 IN length | IN | - | -
Angle440.375 |  |  | Steel, Angle | 9.8 | 0.375 | 4 | 4 | 0.5 | - | YC | 001 08406 404 | Angle Blk 4 x 4 x .38 thk | A36 HRS | R19 | 324 IN length | IN | - | -
Angle640.375 |  |  | Steel, Angle | 12.3 | 0.375 | 6 | 4 | 0.5 | - | YC | 001 07501 064 | Angle Blk 6 x 4 x .38 thk | A36 HRS | R18 | 324 IN length | IN | - | -
Tubing110.065 |  |  | Steel, Tubing | 0.8265 | 0.065 | 1 | 1 | - | - | YC | 001-07517-000 | Tubing 1 X 1 X .065 | A36 | - | 324 IN length | IN | - | -
Tubing330.12 |  |  | Steel, Tubing | 4.58 | 0.12 | 3 | 3 | - | XT | YC | 001-08408-003 | Tubing 3 X 3 X .120 | A36 | - | 324 IN length | IN | - | -
Tubing440.12 |  |  | Steel, Tubing | 6.22 | 0.12 | 4 | 4 | - | - | YC | 001-07519-000 | Tubing 4 X 4 X .120 | A36 | - | 324 IN length | IN | - | -
Tubing220.12 |  |  | Steel, Tubing | 2.94 | 0.12 | 2 | 2 | - | XT | YC | 001-08408-002 | Tubing 2 X 2 X .120 | A36 | - | 324 IN length | IN | - | -
Tubing1.50.750.12 |  |  | Steel, Tubing | 1.64 | 0.12 | 1.5 | 0.75 | - | - | YC | 001 08570 000 | Tubing, Blk 3/4"x1 1/2"x.120 | A36 | - | 324 IN length | IN | - | -
Flat Bar30.25 |  |  | Steel, Flat Bar | 2.975 | 0.25 | - | 3 | - | - | YC | 001-07578-000 | Flat Bar 3 x .25 THK | A36 | - | 324 IN length | IN | - | -
Aluminum, Extruded, Shapes
ALUT12TB |  |  | Alum, Extrude, Track | - | - | - | - | - | XT | - | 008 02326 010 | Track,Fltr,Top/Btm,W/2_Pre | extru. Al. | - | IN length | IN | ALM TRK 12TB | ALUT12TB
ALUT12M- |  |  | Alum, Extrude, Track | - | - | - | - | - | XT | - | 008 02327 010 | Track,Fltr,Mid,W/2_Pre | extru. Al. | - | IN length | IN | ALM TRK 12M | ALUT12M-
ALUT14TB |  |  | Alum, Extrude, Track | - | - | - | - | - | XT | - | 008 02328 010 | Track,Fltr,Top/Btm,W/4_Pre | extru. Al. | - | IN length | IN | ALM TRK 14TB | ALUT14TB
ALUT14M- |  |  | Alum, Extrude, Track | - | - | - | - | - | XT | - | 008 02329 010 | Track,Fltr,Mid,W/4_Pre | extru. Al. | - | IN length | IN | ALM TRK 14M | ALUT14M-
ALUT42TB |  |  | Alum, Extrude, Track | - | - | - | - | - | XT | - | 008 02330 010 | Track,Fltr,Top/Btm,W/2_Pre | extru. Al. | - | IN length | IN | ALM TRK 42TB | ALUT42TB
ALUT42M- |  |  | Alum, Extrude, Track | - | - | - | - | - | XT | - | 008 02331 010 | Track,Fltr,Mid,W/2_Pre | extru. Al. | - | IN length | IN | ALM TRK 42M | ALUT42M-
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02575 001 | Track,Fltr,Hi-Eff,Top/Btm, 2" Pre, Rigid/Bag Final | extru. Al. | - | IN length | IN | - | -
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02576 001 | Track,Fltr,Hi-Eff,Mid, 2" Pre, Rigid/Bag Final | extru. Al. | - | IN length | IN | - | -
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02577 001 | Extrusion,Frame,Outswing,2", YC, 204" L | extru. Al. | - | IN length | IN | - | -
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02578 001 | Extrusion,Frame,Inswing,2", YC, 204" L | extru. Al. | - | IN length | IN | - | -
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02579 001 | Extrusion,Door,2", YC, 204" L | extru. Al. | - | IN length | IN | - | -
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02584 001 | Extrusion,Frame,Tb,Outswing,2", YC, 204" L | extru. Al. | - | IN length | IN | - | -
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02585 001 | Extrusion,Frame,Tb,Inswing,2", YC, 204" | extru. Al. | - | IN length | IN | - | -
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02586 001 | Extrusion,Tb,Door,2", YC,204" L | extru. Al. | - | IN length | IN | - | -
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02587 001 | Extrusion,Frame,Tb,Outswing,3",YC, 204" L | extru. Al. | - | IN length | IN | - | -
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02588 001 | Extrusion,Frame,Tb,Inswing,3", YC, 204" Lg | extru. Al. | - | IN length | IN | - | -
- |  |  | Alum, Extrude, Track | - | - | - | - | - | - | YC | 008 02589 001 | Extrusion,Tb,Door,3", YC, 204" L | extru. Al. | - | IN length | IN | - | -
Copper, Tube
- |  |  | Copper, Tube | - | - | 0.25 | 0.25 | - | - | YC | 007 09019 025 | Tubing,Cu,.25dia | Copper Type L | R80 | IN length | IN | - | -
- |  |  | Copper, Tube | - | 0.02 | 0.625 | 0.625 | - | - | YC | 007-05770-000 | Tube,Cu,.63od_.020thk | Copper Type L | R80 | IN length | IN | - | -
Aluminum, Shapes
TubingAlum1.50.750.125 |  |  | Alum, Tubing | 0.588 | 0.125 | 1.5 | 0.75 | - | - | YC | 008 02595 001 | Tubing, Alum, 0.75x1.50x0.125 | - | - | IN Length | IN | - | -
ChannelAlum108.36 |  |  | Alum, Channel | 8.36 | 0.31 | 10 | 4.25 | 0.5 | - | YC | 008 02592 001 | Channel Aluminum 10x8.36 Lb/Ft | - | - | IN Length | IN | - | -
ChannelAlum1211.82 |  |  | Alum, Channel | 11.82 | 0.35 | 12 | 5 | 0.62 | - | YC | 008 02593 001 | Channel Aluminum 12x11.82lb/Ft | - | - | IN Length | IN | - | -
ChannelAlum64.03 |  |  | Alum, Channel | 4.03 | 0.21 | 6 | 3.25 | 0.35 | - | YC | 008 02590 001 | Channel Aluminum 6x4.03 Lb/Ft | - | - | IN Length | IN | - | -
ChannelAlum85.79 |  |  | Alum, Channel | 5.79 | 0.25 | 8 | 3.75 | 0.41 | - | YC | 008 02591 001 | Channel Aluminum 8x5.79 Lb/Ft | - | - | IN Length | IN | - | -
Steel, Stainless, Shapes
ChannelSST68.27 |  |  | SST, Channel | 8.27 | 0.19 | 6 | 1.92 | - | - | YC | 001-07530-006 | Channel,304ss,6_8.3#/Ft, Flange Width = 1.9" | - | - | IN length | IN | - | -
ChannelSST818.8 |  |  | SST, Channel | 18.8 | 0.487 | 8 | 2.527 | - | - | YC | 001-07530-008 | Channel,304ss,8_18.8#/Ft, Flange Width = 2.53" | - | - | IN length | IN | - | -
TubingSST110.065 |  |  | SST, Tubing | 0.827 | 0.065 | 1 | 1 | - | - | YC | 001-07520-000 | Tubing 1 x 1 x .065 304 SST | A36 | - | 324 IN length | IN | - | -
Steel, Rebar
Rebar0.5 |  |  | Steel, Rebar | 0.668 | - | - | 0.5 | - | - | YC | 001-08653-000 | REBAR .5" RD #4 | - | - | IN length | IN | - | -
Notes:
1. All sheet or coil stock raw material will be calculated in Square Foot, (Width" X Length") / 144 = SQ. FT.
2. Conversions to Pounds or Sheets will be setup in Mapics as a (1 to X) product structure relationship
3. The max sheet size is 60 X 144 inches for sheet stock material
4. With the exception to standard R259 is that all Galvanized Steel will be Chemically Treated and oiled with a mineral based oil which is easily removable by vapor degreasing or mild alkaline cleaning with a hot water rinse.

## Revision List
Revision | Date | Description | By | ECN Number
- | 2015-09-01 | NEW | PS | 15-8548
A | 2016-03-08 | CHANGED ISOLATOR PLATE FROM PURCHASED TO MANUFACTURED/ADDED WELDMENT | PS | 16-8921
B | 2017-10-23 | ADDED QTY OUTPUT TO LOAD CALC TAB FOR ISO PLATES | PS | 17-9501
C | 2018-05-29 | FIXED WEIGHT CALC ISSUES ON TYPE A BASES | PS | 18-9917
D | 2018-07-20 | FIXED TOP TRANSITION HEIGHT CALC | PS | 18-9973
E | 2019-06-14 | Added valid variable list to Data sheet | HLU | 19-10292
F | 2019-08-17 | Added valid variable list to Data sheet | PS | 19-9893
G | 2023-08-10 | Fixed weldment D11 calc (excel calcs B163) | PS | 23-11407
H | 2024-07-02 | Added new named cells FAN_SHAFT_DIAMETER and MOTOR_SHAFT_DIAMETER to Center Distance tab as MOM outputs for belt guard and sheave sizing. | NSC | 24-11646
I | 2025-02-26 | Added part #'s to "Isolator Plate" tab & updated iLogic in the iProperties rules in plate assy's. | JAB | 25-11734
J | 2025-09-19 | Updated Fan shaft diameter values to exact multiples of 1/32" in the "Fan Data" tab | NSC | 24-11646